## Info
Date | 2017-08-21 13:59:50
Manufacturer Name | Pika Energy
Product Name | B-Link
Product Models | B301c
Product Description | Battery converter

## 1, Common
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40002 | ID |  |  | 1
40003 | L |  |  | 66
40004 | Manufacturer (Mn) |  |  | Pika | R
40020 | Model (Md) |  |  | Smart Battery | R | Pika Energy device type (e.g., X7601 Inverter, B301c Battery Converter, S2501 PV Link, etc)
40036 | Options (Opt) |  |  | unimplemented | R | Reserved
40044 | Version (Vr) |  |  |  | R | Device software version
40052 | Serial Number (SN) |  |  |  | R | The 12 digit hexadecimal number unique to the REbus device. This is also known as the RCP (REbus Control Protocol) number. The RCP number for any Pika REbus device is of the format 0001XXXXYYYY, where XXXX corresponds the device type (e.g., 0007 is a Energy Island Inverter) which when combined with the device ID denoted by YYYY, is a unique number specific to that instance of the device.
40068 | Device Address (DA) |  |  | unimplemented | RW
40069 | Pad |  |  |  | R

## 802, Battery base
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40070 | ID |  |  | 802 |  | Battery Base Model
40071 | L |  |  | 62
40072 | Nameplate Charge Capacity (AHRtg) |  |  | supported | R | Nameplate charge capacity in amp-hours.
40073 | Nameplate Energy Capacity (WHRtg) |  |  | supported | R | Nameplate energy capacity in DC watt-hours.
40074 | Nameplate Max Charge Rate (WChaRteMax) |  |  | supported | R | Maximum rate of energy transfer into the storage device in DC watts.
40075 | Namplate Max Discharge Rate (WDisChaRteMax) |  |  | supported | R | Maximum rate of energy transfer out of the storage device in DC watts.
40076 | Self Discharge Rate (DisChaRte) |  |  | unimplemented | R | Self discharge rate. Percentage of capacity (WHRtg) discharged per day.
40077 | Nameplate Max SoC (SoCMax) |  |  | supported | RW | Manufacturer maximum state of charge, expressed as a percentage.
40078 | Nameplate Min SoC (SoCMin) |  |  | supported | RW | Manufacturer minimum state of charge, expressed as a percentage.
40079 | Max Reserve Percent (SocRsvMax) |  |  | supported | RW | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage.
40080 | Min Reserve Percent (SoCRsvMin) |  |  | supported | RW | Setpoint for minimum reserve for storage as a percentage of the nominal maximum storage.
40081 | State of Charge (SoC) |  |  | supported | R | State of charge, expressed as a percentage.
40082 | Depth of Discharge (DoD) |  |  | unimplemented | R | Depth of discharge, expressed as a percentage.
40083 | State of Health (SoH) |  |  | supported | R | Percentage of battery life remaining.
40084 | Cycle Count (NCyc) |  |  | unimplemented | R | Number of cycles executed in the battery.
40086 | Charge Status (ChaSt) |  |  | unimplemented | R | Charge status of storage device. Enumeration.
|  |  | OFF | supported
|  |  | EMPTY | supported
|  |  | DISCHARGING | supported
|  |  | CHARGING | supported
|  |  | FULL | supported
|  |  | HOLDING | supported
|  |  | TESTING | supported
40087 | Control Mode (LocRemCtl) |  |  | unimplemented | R | Battery control mode. Enumeration.
|  |  | Remote Control (REMOTE) | supported
|  |  | Local Control (LOCAL) | supported
40088 | Battery Heartbeat (Hb) |  |  | unimplemented | R | Value is incremented every second with periodic resets to zero.
40089 | Controller Heartbeat (CtrlHb) |  |  | unimplemented | RW | Value is incremented every second with periodic resets to zero.
40090 | Alarm Reset (AlmRst) |  |  | unimplemented | RW | Used to reset any latched alarms. 1 = Reset.
40091 | Battery Type (Typ) |  |  | supported | R | Type of battery. Enumeration.
|  |  | Not Applicable or Unknown (NOT APPLICABLE_UNKNOWN) | supported
|  |  | Lead-Acid (LEAD_ACID) | supported
|  |  | Nickel-Metal Hydrate (NICKEL_METAL_HYDRATE) | supported
|  |  | Nickel-Cadmium (NICKEL_CADMIUM) | supported
|  |  | Lithium-Ion (LITHIUM_ION) | supported
|  |  | Carbon-Zinc (CARBON_ZINC) | supported
|  |  | Zinc Chloride (ZINC_CHLORIDE) | supported
|  |  | Alkaline (ALKALINE) | supported
|  |  | Rechargeable Alkaline (RECHARGEABLE_ALKALINE) | supported
|  |  | Sodium-Sulfur (SODIUM_SULFUR) | supported
|  |  | Flow (FLOW) | supported
|  |  | Other (OTHER) | supported
40092 | State of the Battery Bank (State) |  |  | supported | R | State of the battery bank. Enumeration.
|  |  | Disconnected (DISCONNECTED) | supported
|  |  | Initializing (INITIALIZING) | supported
|  |  | Connected (CONNECTED) | supported
|  |  | Standby (STANDBY) | supported
|  |  | SoC Protection (SOC PROTECTION) | supported
|  |  | Fault (FAULT) | supported
40093 | Pad (Pad1) |  |  |  | R | Pad register.
40094 | Warranty Date (WarrDt) |  |  | unimplemented | R | Date the device warranty expires.
40096 | Battery Event 1 Bitfield (Evt1) |  |  | unimplemented | R | Alarms and warnings. Bit flags.
|  |  | Communication Error (COMMUNICATION_ERROR) | supported
|  |  | Over Temperature Alarm (OVER_TEMP_ALARM) | supported
|  |  | Over Temperature Warning (OVER_TEMP_WARNING) | supported
|  |  | Under Temperature Alarm (UNDER_TEMP_ALARM) | supported
|  |  | Under Temperature Warning (UNDER_TEMP_WARNING) | supported
|  |  | Over Charge Current Alarm (OVER_CHARGE_CURRENT_ALARM) | supported
|  |  | Over Charge Current Warning (OVER_CHARGE_CURRENT_WARNING) | supported
|  |  | Over Discharge Current Alarm (OVER_DISCHARGE_CURRENT_ALARM) | supported
|  |  | Over Discharge Current Warning (OVER_DISCHARGE_CURRENT_WARNING) | supported
|  |  | Over Voltage Alarm (OVER_VOLT_ALARM) | supported
|  |  | Over Voltage Warning (OVER_VOLT_WARNING) | supported
|  |  | Under Voltage Alarm (UNDER_VOLT_ALARM) | supported
|  |  | Under Voltage Warning (UNDER_VOLT_WARNING) | supported
|  |  | Under State of Charge Min Alarm (UNDER_SOC_MIN_ALARM) | supported
|  |  | Under State of Charge Min Warning (UNDER_SOC_MIN_WARNING) | supported
|  |  | Over State of Charge Max Alarm (OVER_SOC_MAX_ALARM) | supported
|  |  | Over State of Charge Max Warning (OVER_SOC_MAX_WARNING) | supported
|  |  | Voltage Imbalance Warning (VOLTAGE_IMBALANCE_WARNING) | supported
|  |  | Temperature Imbalance Alarm (TEMPERATURE_IMBALANCE_ALARM) | supported
|  |  | Temperature Imbalance Warning (TEMPERATURE_IMBALANCE_WARNING) | supported
|  |  | Contactor Error (CONTACTOR_ERROR) | supported
|  |  | Fan Error (FAN_ERROR) | supported
|  |  | Ground Fault Error (GROUND_FAULT) | supported
|  |  | Open Door Error (OPEN_DOOR_ERROR) | supported
|  |  | Current Imbalance Warning (CURRENT_IMBALANCE_WARNING) | supported
|  |  | Other Battery Alarm (OTHER_ALARM) | supported
|  |  | Other Battery Warning (OTHER_WARNING) | supported
40098 | Battery Event 2 Bitfield (Evt2) |  |  | unimplemented | R | Alarms and warnings. Bit flags.
40100 | Vendor Event Bitfield 1 (EvtVnd1) |  |  | supported | R | Vendor defined events.
40102 | Vendor Event Bitfield 2 (EvtVnd2) |  |  | supported | R | Vendor defined events.
40104 | External Battery Voltage (V) |  |  | supported | R | DC Bus Voltage.
40105 | Max Battery Voltage (VMax) |  |  | unimplemented | R | Instantaneous maximum battery voltage.
40106 | Min Battery Voltage (VMin) |  |  | unimplemented | R | Instantaneous minimum battery voltage.
40107 | Max Cell Voltage (CellVMax) |  |  | supported | R | Maximum voltage for all cells in the bank.
40108 | Max Cell Voltage String (CellVMaxStr) |  |  | unimplemented | R | String containing the cell with maximum voltage.
40109 | Max Cell Voltage Module (CellVMaxMod) |  |  | unimplemented | R | Module containing the cell with maximum voltage.
40110 | Min Cell Voltage (CellVMin) |  |  | supported | R | Minimum voltage for all cells in the bank.
40111 | Min Cell Voltage String (CellVMinStr) |  |  | unimplemented | R | String containing the cell with minimum voltage.
40112 | Min Cell Voltage Module (CellVMinMod) |  |  | unimplemented | R | Module containing the cell with minimum voltage.
40113 | Average Cell Voltage (CellVAvg) |  |  | unimplemented | R | Average cell voltage for all cells in the bank.
40114 | Total DC Current (A) |  |  | supported | R | Total DC current flowing to/from the battery bank.
40115 | Max Charge Current (AChaMax) |  |  | supported | RW | Instantaneous maximum DC charge current.
40116 | Max Discharge Current (ADisChaMax) |  |  | supported | RW | Instantaneous maximum DC discharge current.
40117 | Total Power (W) |  |  | supported | R | Total power flowing to/from the battery bank.
40118 | Inverter State Request (ReqInvState) |  |  | unimplemented | R | Request from battery to start or stop the inverter. Enumeration.
|  |  | No Request (NO REQUEST) | supported
|  |  | Start Inverter (START) | supported
|  |  | Stop Inverter (STOP) | supported
40119 | Battery Power Request (ReqW) |  |  | unimplemented | R | AC Power requested by battery.
40120 | Set Operation (SetOp) |  |  | unimplemented | RW | Instruct the battery bank to perform an operation such as connecting. Enumeration.
|  |  | Connect the Battery Bank (CONNECT) | supported
|  |  | Disconnect the Battery Bank (DISCONNECT) | supported
40121 | Set Inverter State (SetInvState) |  |  | unimplemented | RW | Set the current state of the inverter.
|  |  | Inverter is Stopped (INVERTER_STOPPED) | supported
|  |  | Inverter is in Standby (INVERTER_STANDBY) | supported
|  |  | Inverter is Started (INVERTER_STARTED) | supported
40122 | AHRtg_SF |  |  | -2 | R | Scale factor for charge capacity.
40123 | WHRtg_SF |  |  | 0 | R | Scale factor for energy capacity.
40124 | WChaDisChaMax_SF |  |  | 0 | R | Scale factor for maximum charge and discharge rate.
40125 | DisChaRte_SF |  |  | 0 | R | Scale factor for self discharge rate.
40126 | SoC_SF |  |  | -1 | R | Scale factor for state of charge values.
40127 | DoD_SF |  |  | 0 | R | Scale factor for depth of discharge.
40128 | SoH_SF |  |  | -1 | R | Scale factor for state of health.
40129 | V_SF |  |  | -1 | R | Scale factor for DC bus voltage.
40130 | CellV_SF |  |  | -3 | R | Scale factor for cell voltage.
40131 | A_SF |  |  | -2 | R | Scale factor for DC current.
40132 | AMax_SF |  |  | -2 | R | Scale factor for instantationous DC charge/discharge current.
40133 | W_SF |  |  | 0 | R | Scale factor for AC power request.