## Introduction
SunSpec PICS Template
This SunSpec PICS template was generated by SunSpec Dashboard v1.0.5 based on the model contents of the connected device.
This spreadsheet describes the Modbus mapping for the Pika Energy X7600 series inverter as of 10/24/2017
Please contact Pika Energy before embarking on an integration project to ensure the most up-to-date mapping.

## 1
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40002 | ID |  |  | 1
40003 | L |  |  | 66
40004 | Manufacturer (Mn) |  |  | Pika | R
40020 | Model (Md) |  |  | X7601 Islanding Inverter | R
40036 | Options (Opt) |  |  | unimplemented | R
40044 | Version (Vr) |  |  | 132_11581 | R
40052 | Serial Number (SN) |  |  | 000100070096 | R
40068 | Device Address (DA) |  |  | unimplemented | RW
40069 | Pad |  |  |  | R

## 102
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40070 | ID |  |  | 102
40071 | L |  |  | 50
40072 | Amps (A) |  |  | supported | R
40073 | Amps PhaseA (AphA) |  |  | supported | R
40074 | Amps PhaseB (AphB) |  |  | supported | R
40075 | Amps PhaseC (AphC) |  |  | unimplemented | R
40076 | A_SF |  |  | -2 | R
40077 | Phase Voltage AB (PPVphAB) |  |  | unimplemented | R
40078 | Phase Voltage BC (PPVphBC) |  |  | unimplemented | R
40079 | Phase Voltage CA (PPVphCA) |  |  | unimplemented | R
40080 | Phase Voltage AN (PhVphA) |  |  | supported | R
40081 | Phase Voltage BN (PhVphB) |  |  | supported | R
40082 | Phase Voltage CN (PhVphC) |  |  | unimplemented | R
40083 | V_SF |  |  | -1 | R
40084 | Watts (W) |  |  | supported | R
40085 | W_SF |  |  | 0 | R
40086 | Hz |  |  | supported | R
40087 | Hz_SF |  |  | -2 | R
40088 | VA |  |  | supported | R
40089 | VA_SF |  |  | 0 | R
40090 | VAr |  |  | supported | R
40091 | VAr_SF |  |  | 0 | R
40092 | PF |  |  | supported | R
40093 | PF_SF |  |  | -1 | R
40094 | WattHours (WH) |  |  | supported | R
40096 | WH_SF |  |  | 0 | R
40097 | DC Amps (DCA) |  |  | unimplemented | R
40098 | DCA_SF |  |  | 0 | R
40099 | DC Voltage (DCV) |  |  | supported | R
40100 | DCV_SF |  |  | -1 | R
40101 | DC Watts (DCW) |  |  | unimplemented | R
40102 | DCW_SF |  |  | 0 | R
40103 | Cabinet Temperature (TmpCab) |  |  | supported | R
40104 | Heat Sink Temperature (TmpSnk) |  |  | supported | R
40105 | Transformer Temperature (TmpTrns) |  |  | supported | R
40106 | Other Temperature (TmpOt) |  |  | supported | R
40107 | Tmp_SF |  |  | -1 | R
40108 | Operating State (St) |  |  | supported | R
|  |  | Off (OFF) | supported
|  |  | Sleeping (SLEEPING) | supported
|  |  | Starting (STARTING) | supported
|  |  | MPPT | supported
|  |  | Throttled (THROTTLED) | supported
|  |  | Shutting down (SHUTTING_DOWN) | supported
|  |  | Fault (FAULT) | supported
|  |  | Standby (STANDBY) | supported
40109 | Vendor Operating State (StVnd) |  |  | supported | R
40110 | Event1 (Evt1) |  |  | supported | R
|  |  | Ground fault (GROUND_FAULT) | supported
|  |  | DC over voltage (DC_OVER_VOLT) | supported
|  |  | AC disconnect open (AC_DISCONNECT) | supported
|  |  | DC disconnect open (DC_DISCONNECT) | supported
|  |  | Grid shutdown (GRID_DISCONNECT) | supported
|  |  | Cabinet open (CABINET_OPEN) | supported
|  |  | Manual shutdown (MANUAL_SHUTDOWN) | supported
|  |  | Over temperature (OVER_TEMP) | supported
|  |  | Frequency above limit (OVER_FREQUENCY) | supported
|  |  | Frequency under limit (UNDER_FREQUENCY) | supported
|  |  | AC Voltage above limit (AC_OVER_VOLT) | supported
|  |  | AC Voltage under limit (AC_UNDER_VOLT) | supported
|  |  | Blown String fuse on input (BLOWN_STRING_FUSE) | supported
|  |  | Under temperature (UNDER_TEMP) | supported
|  |  | Generic Memory or Communication error (internal) (MEMORY_LOSS) | supported
|  |  | Hardware test failure (HW_TEST_FAILURE) | supported
40112 | Event Bitfield 2 (Evt2) |  |  | supported | R
40114 | Vendor Event Bitfield 1 (EvtVnd1) |  |  | supported | R
40116 | Vendor Event Bitfield 2 (EvtVnd2) |  |  | supported | R
40118 | Vendor Event Bitfield 3 (EvtVnd3) |  |  | supported | R
40120 | Vendor Event Bitfield 4 (EvtVnd4) |  |  | supported | R

## 64204
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40122 | ID |  |  | 64204
40123 | L |  |  | 8
40124 | Power export line 1 (Px1) |  |  | supported | R
40125 | Power export line 2 (Px2) |  |  | supported | R
40126 | Power export line 3 (Px3) |  |  | supported | R
40127 | Energy exported (Whx) |  |  | supported | R
40129 | Energy imported (Whin) |  |  | supported | R
40131 | Pad |  |  |  | R

## 64202
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40132 | ID |  |  | 64202
40133 | L |  |  | 12
40134 | System Operating Mode (SysMd) |  |  | supported | R
|  |  | SAFETY_SHUTDOWN | supported
|  |  | GRID_CONNECT | supported
|  |  | SELF_SUPPLY | supported
|  |  | CLEAN_BACKUP | supported
|  |  | PRIORITY_BACKUP | supported
|  |  | ARBITRAGE | supported
40135 | Max real power (PMax) |  |  | supported | RW
40136 | Max reactive power (QMax) |  |  | supported | RW
40137 | Real power target (PMaxLimPct) |  |  | supported | RW
40138 | Reactive power target (QMaxLimPct) |  |  | supported | RW
40139 | Ramp rate (PQGra) |  |  | supported | RW
40140 | PQMax_SF |  |  | 0 | R
40141 | PQLimPct_SF |  |  | -1 | R
40142 | PQGra_SF |  |  | 0 | R
40143 | Control priority (CtlPr) |  |  | supported | RW
|  |  | REAL | supported
|  |  | REACTIVE | supported
40144 | Enable arbitrage control (PQSet_Ena) |  |  | supported | RW
|  |  | DISABLE | supported
|  |  | ENABLE | supported
|  |  | UPDATE | supported
40145 | Connect (Conn) |  |  | supported | RW
|  |  | DISCONNECT | supported
|  |  | CONNECT | supported

## 120
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40146 | ID |  |  | 120
40147 | L |  |  | 26
40148 | DERTyp |  |  | supported | R
|  |  | PV | supported
|  |  | PV_STOR | supported
40149 | WRtg |  |  | supported | R
40150 | WRtg_SF |  |  | 0 | R
40151 | VARtg |  |  | supported | R
40152 | VARtg_SF |  |  | 0 | R
40153 | VArRtgQ1 |  |  | supported | R
40154 | VArRtgQ2 |  |  | supported | R
40155 | VArRtgQ3 |  |  | supported | R
40156 | VArRtgQ4 |  |  | supported | R
40157 | VArRtg_SF |  |  | 0 | R
40158 | ARtg |  |  | supported | R
40159 | ARtg_SF |  |  | -2 | R
40160 | PFRtgQ1 |  |  | supported | R
40161 | PFRtgQ2 |  |  | supported | R
40162 | PFRtgQ3 |  |  | supported | R
40163 | PFRtgQ4 |  |  | supported | R
40164 | PFRtg_SF |  |  | -3 | R
40165 | WHRtg |  |  | unimplemented | R
40166 | WHRtg_SF |  |  | 0 | R
40167 | AhrRtg |  |  | unimplemented | R
40168 | AhrRtg_SF |  |  | 0 | R
40169 | MaxChaRte |  |  | unimplemented | R
40170 | MaxChaRte_SF |  |  | 0 | R
40171 | MaxDisChaRte |  |  | unimplemented | R
40172 | MaxDisChaRte_SF |  |  | 0 | R
40173 | Pad |  |  |  | R

## 123
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40174 | ID |  |  | 123
40175 | L |  |  | 24
40176 | Conn_WinTms |  |  | unimplemented | RW
40177 | Conn_RvrtTms |  |  | unimplemented | RW
40178 | Conn |  |  | supported | RW
|  |  | DISCONNECT | supported
|  |  | CONNECT | supported
40179 | WMaxLimPct |  |  | supported | RW
40180 | WMaxLimPct_WinTms |  |  | unimplemented | RW
40181 | WMaxLimPct_RvrtTms |  |  | unimplemented | RW
40182 | WMaxLimPct_RmpTms |  |  | unimplemented | RW
40183 | WMaxLim_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40184 | OutPFSet |  |  | supported | RW
40185 | OutPFSet_WinTms |  |  | unimplemented | RW
40186 | OutPFSet_RvrtTms |  |  | unimplemented | RW
40187 | OutPFSet_RmpTms |  |  | unimplemented | RW
40188 | OutPFSet_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40189 | VArWMaxPct |  |  | unimplemented | RW
40190 | VArMaxPct |  |  | supported | RW
40191 | VArAvalPct |  |  | unimplemented | RW
40192 | VArPct_WinTms |  |  | unimplemented | RW
40193 | VArPct_RvrtTms |  |  | unimplemented | RW
40194 | VArPct_RmpTms |  |  | unimplemented | RW
40195 | VArPct_Mod |  |  | unimplemented | RW
|  |  | NONE | supported
|  |  | WMax | supported
|  |  | VArMax | supported
|  |  | VArAval | supported
40196 | VArPct_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40197 | WMaxLimPct_SF |  |  | -1 | R
40198 | OutPFSet_SF |  |  | -3 | R
40199 | VArPct_SF |  |  | -1 | R

## 126
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40200 | ID |  |  | 126
40201 | L |  |  | 226
40202 | ActCrv |  |  | supported | RW
40203 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40204 | WinTms |  |  | unimplemented | RW
40205 | RvrtTms |  |  | unimplemented | RW
40206 | RmpTms |  |  | unimplemented | RW
40207 | NCrv |  |  | supported | R
40208 | NPt |  |  | supported | R
40209 | V_SF |  |  | -1 | R
40210 | DeptRef_SF |  |  | -1 | R
40211 | RmpIncDec_SF |  |  | 0 | R
40212 | ActPt | 1 |  | supported | RW
40213 | DeptRef | 1 |  | supported | RW
|  |  | WMax | supported
|  |  | VArMax | supported
|  |  | VArAval | supported
40214 | V1 | 1 |  | supported | RW
40215 | VAr1 | 1 |  | supported | RW
40216 | V2 | 1 |  | supported | RW
40217 | VAr2 | 1 |  | supported | RW
40218 | V3 | 1 |  | supported | RW
40219 | VAr3 | 1 |  | supported | RW
40220 | V4 | 1 |  | supported | RW
40221 | VAr4 | 1 |  | supported | RW
40222 | V5 | 1 |  | supported | RW
40223 | VAr5 | 1 |  | supported | RW
40224 | V6 | 1 |  | supported | RW
40225 | VAr6 | 1 |  | supported | RW
40226 | V7 | 1 |  | supported | RW
40227 | VAr7 | 1 |  | supported | RW
40228 | V8 | 1 |  | supported | RW
40229 | VAr8 | 1 |  | supported | RW
40230 | V9 | 1 |  | supported | RW
40231 | VAr9 | 1 |  | supported | RW
40232 | V10 | 1 |  | supported | RW
40233 | VAr10 | 1 |  | supported | RW
40234 | V11 | 1 |  | unimplemented | RW
40235 | VAr11 | 1 |  | unimplemented | RW
40236 | V12 | 1 |  | unimplemented | RW
40237 | VAr12 | 1 |  | unimplemented | RW
40238 | V13 | 1 |  | unimplemented | RW
40239 | VAr13 | 1 |  | unimplemented | RW
40240 | V14 | 1 |  | unimplemented | RW
40241 | VAr14 | 1 |  | unimplemented | RW
40242 | V15 | 1 |  | unimplemented | RW
40243 | VAr15 | 1 |  | unimplemented | RW
40244 | V16 | 1 |  | unimplemented | RW
40245 | VAr16 | 1 |  | unimplemented | RW
40246 | V17 | 1 |  | unimplemented | RW
40247 | VAr17 | 1 |  | unimplemented | RW
40248 | V18 | 1 |  | unimplemented | RW
40249 | VAr18 | 1 |  | unimplemented | RW
40250 | V19 | 1 |  | unimplemented | RW
40251 | VAr19 | 1 |  | unimplemented | RW
40252 | V20 | 1 |  | unimplemented | RW
40253 | VAr20 | 1 |  | unimplemented | RW
40254 | CrvNam | 1 |  | unimplemented | RW
40262 | RmpTms | 1 |  | unimplemented | RW
40263 | RmpDecTmm | 1 |  | unimplemented | RW
40264 | RmpIncTmm | 1 |  | unimplemented | RW
40265 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
40266 | ActPt | 2 |  | supported | RW
40267 | DeptRef | 2 |  | supported | RW
40268 | V1 | 2 |  | supported | RW
40269 | VAr1 | 2 |  | supported | RW
40270 | V2 | 2 |  | supported | RW
40271 | VAr2 | 2 |  | supported | RW
40272 | V3 | 2 |  | supported | RW
40273 | VAr3 | 2 |  | supported | RW
40274 | V4 | 2 |  | supported | RW
40275 | VAr4 | 2 |  | supported | RW
40276 | V5 | 2 |  | supported | RW
40277 | VAr5 | 2 |  | supported | RW
40278 | V6 | 2 |  | supported | RW
40279 | VAr6 | 2 |  | supported | RW
40280 | V7 | 2 |  | supported | RW
40281 | VAr7 | 2 |  | supported | RW
40282 | V8 | 2 |  | supported | RW
40283 | VAr8 | 2 |  | supported | RW
40284 | V9 | 2 |  | supported | RW
40285 | VAr9 | 2 |  | supported | RW
40286 | V10 | 2 |  | supported | RW
40287 | VAr10 | 2 |  | supported | RW
40288 | V11 | 2 |  | unimplemented | RW
40289 | VAr11 | 2 |  | unimplemented | RW
40290 | V12 | 2 |  | unimplemented | RW
40291 | VAr12 | 2 |  | unimplemented | RW
40292 | V13 | 2 |  | unimplemented | RW
40293 | VAr13 | 2 |  | unimplemented | RW
40294 | V14 | 2 |  | unimplemented | RW
40295 | VAr14 | 2 |  | unimplemented | RW
40296 | V15 | 2 |  | unimplemented | RW
40297 | VAr15 | 2 |  | unimplemented | RW
40298 | V16 | 2 |  | unimplemented | RW
40299 | VAr16 | 2 |  | unimplemented | RW
40300 | V17 | 2 |  | unimplemented | RW
40301 | VAr17 | 2 |  | unimplemented | RW
40302 | V18 | 2 |  | unimplemented | RW
40303 | VAr18 | 2 |  | unimplemented | RW
40304 | V19 | 2 |  | unimplemented | RW
40305 | VAr19 | 2 |  | unimplemented | RW
40306 | V20 | 2 |  | unimplemented | RW
40307 | VAr20 | 2 |  | unimplemented | RW
40308 | CrvNam | 2 |  | unimplemented | RW
40316 | RmpTms | 2 |  | unimplemented | RW
40317 | RmpDecTmm | 2 |  | unimplemented | RW
40318 | RmpIncTmm | 2 |  | unimplemented | RW
40319 | ReadOnly | 2 |  | supported | R
40320 | ActPt | 3 |  | supported | RW
40321 | DeptRef | 3 |  | supported | RW
40322 | V1 | 3 |  | supported | RW
40323 | VAr1 | 3 |  | supported | RW
40324 | V2 | 3 |  | supported | RW
40325 | VAr2 | 3 |  | supported | RW
40326 | V3 | 3 |  | supported | RW
40327 | VAr3 | 3 |  | supported | RW
40328 | V4 | 3 |  | supported | RW
40329 | VAr4 | 3 |  | supported | RW
40330 | V5 | 3 |  | supported | RW
40331 | VAr5 | 3 |  | supported | RW
40332 | V6 | 3 |  | supported | RW
40333 | VAr6 | 3 |  | supported | RW
40334 | V7 | 3 |  | supported | RW
40335 | VAr7 | 3 |  | supported | RW
40336 | V8 | 3 |  | supported | RW
40337 | VAr8 | 3 |  | supported | RW
40338 | V9 | 3 |  | supported | RW
40339 | VAr9 | 3 |  | supported | RW
40340 | V10 | 3 |  | supported | RW
40341 | VAr10 | 3 |  | supported | RW
40342 | V11 | 3 |  | unimplemented | RW
40343 | VAr11 | 3 |  | unimplemented | RW
40344 | V12 | 3 |  | unimplemented | RW
40345 | VAr12 | 3 |  | unimplemented | RW
40346 | V13 | 3 |  | unimplemented | RW
40347 | VAr13 | 3 |  | unimplemented | RW
40348 | V14 | 3 |  | unimplemented | RW
40349 | VAr14 | 3 |  | unimplemented | RW
40350 | V15 | 3 |  | unimplemented | RW
40351 | VAr15 | 3 |  | unimplemented | RW
40352 | V16 | 3 |  | unimplemented | RW
40353 | VAr16 | 3 |  | unimplemented | RW
40354 | V17 | 3 |  | unimplemented | RW
40355 | VAr17 | 3 |  | unimplemented | RW
40356 | V18 | 3 |  | unimplemented | RW
40357 | VAr18 | 3 |  | unimplemented | RW
40358 | V19 | 3 |  | unimplemented | RW
40359 | VAr19 | 3 |  | unimplemented | RW
40360 | V20 | 3 |  | unimplemented | RW
40361 | VAr20 | 3 |  | unimplemented | RW
40362 | CrvNam | 3 |  | unimplemented | RW
40370 | RmpTms | 3 |  | unimplemented | RW
40371 | RmpDecTmm | 3 |  | unimplemented | RW
40372 | RmpIncTmm | 3 |  | unimplemented | RW
40373 | ReadOnly | 3 |  | supported | R
40374 | ActPt | 4 |  | supported | RW
40375 | DeptRef | 4 |  | supported | RW
40376 | V1 | 4 |  | supported | RW
40377 | VAr1 | 4 |  | supported | RW
40378 | V2 | 4 |  | supported | RW
40379 | VAr2 | 4 |  | supported | RW
40380 | V3 | 4 |  | supported | RW
40381 | VAr3 | 4 |  | supported | RW
40382 | V4 | 4 |  | supported | RW
40383 | VAr4 | 4 |  | supported | RW
40384 | V5 | 4 |  | supported | RW
40385 | VAr5 | 4 |  | supported | RW
40386 | V6 | 4 |  | supported | RW
40387 | VAr6 | 4 |  | supported | RW
40388 | V7 | 4 |  | supported | RW
40389 | VAr7 | 4 |  | supported | RW
40390 | V8 | 4 |  | supported | RW
40391 | VAr8 | 4 |  | supported | RW
40392 | V9 | 4 |  | supported | RW
40393 | VAr9 | 4 |  | supported | RW
40394 | V10 | 4 |  | supported | RW
40395 | VAr10 | 4 |  | supported | RW
40396 | V11 | 4 |  | unimplemented | RW
40397 | VAr11 | 4 |  | unimplemented | RW
40398 | V12 | 4 |  | unimplemented | RW
40399 | VAr12 | 4 |  | unimplemented | RW
40400 | V13 | 4 |  | unimplemented | RW
40401 | VAr13 | 4 |  | unimplemented | RW
40402 | V14 | 4 |  | unimplemented | RW
40403 | VAr14 | 4 |  | unimplemented | RW
40404 | V15 | 4 |  | unimplemented | RW
40405 | VAr15 | 4 |  | unimplemented | RW
40406 | V16 | 4 |  | unimplemented | RW
40407 | VAr16 | 4 |  | unimplemented | RW
40408 | V17 | 4 |  | unimplemented | RW
40409 | VAr17 | 4 |  | unimplemented | RW
40410 | V18 | 4 |  | unimplemented | RW
40411 | VAr18 | 4 |  | unimplemented | RW
40412 | V19 | 4 |  | unimplemented | RW
40413 | VAr19 | 4 |  | unimplemented | RW
40414 | V20 | 4 |  | unimplemented | RW
40415 | VAr20 | 4 |  | unimplemented | RW
40416 | CrvNam | 4 |  | unimplemented | RW
40424 | RmpTms | 4 |  | unimplemented | RW
40425 | RmpDecTmm | 4 |  | unimplemented | RW
40426 | RmpIncTmm | 4 |  | unimplemented | RW
40427 | ReadOnly | 4 |  | supported | R

## 129
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40428 | ID |  |  | 129
40429 | L |  |  | 210
40430 | ActCrv |  |  | supported | RW
40431 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40432 | WinTms |  |  | unimplemented | RW
40433 | RvrtTms |  |  | unimplemented | RW
40434 | RmpTms |  |  | unimplemented | RW
40435 | NCrv |  |  | supported | R
40436 | NPt |  |  | supported | R
40437 | Tms_SF |  |  | -2 | R
40438 | V_SF |  |  | -1 | R
40439 | Pad |  |  |  | R
40440 | ActPt | 1 |  | supported | RW
40441 | Tms1 | 1 |  | supported | RW
40442 | V1 | 1 |  | supported | RW
40443 | Tms2 | 1 |  | supported | RW
40444 | V2 | 1 |  | supported | RW
40445 | Tms3 | 1 |  | supported | RW
40446 | V3 | 1 |  | supported | RW
40447 | Tms4 | 1 |  | supported | RW
40448 | V4 | 1 |  | supported | RW
40449 | Tms5 | 1 |  | supported | RW
40450 | V5 | 1 |  | supported | RW
40451 | Tms6 | 1 |  | supported | RW
40452 | V6 | 1 |  | supported | RW
40453 | Tms7 | 1 |  | supported | RW
40454 | V7 | 1 |  | supported | RW
40455 | Tms8 | 1 |  | supported | RW
40456 | V8 | 1 |  | supported | RW
40457 | Tms9 | 1 |  | supported | RW
40458 | V9 | 1 |  | supported | RW
40459 | Tms10 | 1 |  | supported | RW
40460 | V10 | 1 |  | supported | RW
40461 | Tms11 | 1 |  | unimplemented | RW
40462 | V11 | 1 |  | unimplemented | RW
40463 | Tms12 | 1 |  | unimplemented | RW
40464 | V12 | 1 |  | unimplemented | RW
40465 | Tms13 | 1 |  | unimplemented | RW
40466 | V13 | 1 |  | unimplemented | RW
40467 | Tms14 | 1 |  | unimplemented | RW
40468 | V14 | 1 |  | unimplemented | RW
40469 | Tms15 | 1 |  | unimplemented | RW
40470 | V15 | 1 |  | unimplemented | RW
40471 | Tms16 | 1 |  | unimplemented | RW
40472 | V16 | 1 |  | unimplemented | RW
40473 | Tms17 | 1 |  | unimplemented | RW
40474 | V17 | 1 |  | unimplemented | RW
40475 | Tms18 | 1 |  | unimplemented | RW
40476 | V18 | 1 |  | unimplemented | RW
40477 | Tms19 | 1 |  | unimplemented | RW
40478 | V19 | 1 |  | unimplemented | RW
40479 | Tms20 | 1 |  | unimplemented | RW
40480 | V20 | 1 |  | unimplemented | RW
40481 | CrvNam | 1 |  | unimplemented | RW
40489 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
40490 | ActPt | 2 |  | supported | RW
40491 | Tms1 | 2 |  | supported | RW
40492 | V1 | 2 |  | supported | RW
40493 | Tms2 | 2 |  | supported | RW
40494 | V2 | 2 |  | supported | RW
40495 | Tms3 | 2 |  | supported | RW
40496 | V3 | 2 |  | supported | RW
40497 | Tms4 | 2 |  | supported | RW
40498 | V4 | 2 |  | supported | RW
40499 | Tms5 | 2 |  | supported | RW
40500 | V5 | 2 |  | supported | RW
40501 | Tms6 | 2 |  | supported | RW
40502 | V6 | 2 |  | supported | RW
40503 | Tms7 | 2 |  | supported | RW
40504 | V7 | 2 |  | supported | RW
40505 | Tms8 | 2 |  | supported | RW
40506 | V8 | 2 |  | supported | RW
40507 | Tms9 | 2 |  | supported | RW
40508 | V9 | 2 |  | supported | RW
40509 | Tms10 | 2 |  | supported | RW
40510 | V10 | 2 |  | supported | RW
40511 | Tms11 | 2 |  | unimplemented | RW
40512 | V11 | 2 |  | unimplemented | RW
40513 | Tms12 | 2 |  | unimplemented | RW
40514 | V12 | 2 |  | unimplemented | RW
40515 | Tms13 | 2 |  | unimplemented | RW
40516 | V13 | 2 |  | unimplemented | RW
40517 | Tms14 | 2 |  | unimplemented | RW
40518 | V14 | 2 |  | unimplemented | RW
40519 | Tms15 | 2 |  | unimplemented | RW
40520 | V15 | 2 |  | unimplemented | RW
40521 | Tms16 | 2 |  | unimplemented | RW
40522 | V16 | 2 |  | unimplemented | RW
40523 | Tms17 | 2 |  | unimplemented | RW
40524 | V17 | 2 |  | unimplemented | RW
40525 | Tms18 | 2 |  | unimplemented | RW
40526 | V18 | 2 |  | unimplemented | RW
40527 | Tms19 | 2 |  | unimplemented | RW
40528 | V19 | 2 |  | unimplemented | RW
40529 | Tms20 | 2 |  | unimplemented | RW
40530 | V20 | 2 |  | unimplemented | RW
40531 | CrvNam | 2 |  | unimplemented | RW
40539 | ReadOnly | 2 |  | supported | R
40540 | ActPt | 3 |  | supported | RW
40541 | Tms1 | 3 |  | supported | RW
40542 | V1 | 3 |  | supported | RW
40543 | Tms2 | 3 |  | supported | RW
40544 | V2 | 3 |  | supported | RW
40545 | Tms3 | 3 |  | supported | RW
40546 | V3 | 3 |  | supported | RW
40547 | Tms4 | 3 |  | supported | RW
40548 | V4 | 3 |  | supported | RW
40549 | Tms5 | 3 |  | supported | RW
40550 | V5 | 3 |  | supported | RW
40551 | Tms6 | 3 |  | supported | RW
40552 | V6 | 3 |  | supported | RW
40553 | Tms7 | 3 |  | supported | RW
40554 | V7 | 3 |  | supported | RW
40555 | Tms8 | 3 |  | supported | RW
40556 | V8 | 3 |  | supported | RW
40557 | Tms9 | 3 |  | supported | RW
40558 | V9 | 3 |  | supported | RW
40559 | Tms10 | 3 |  | supported | RW
40560 | V10 | 3 |  | supported | RW
40561 | Tms11 | 3 |  | unimplemented | RW
40562 | V11 | 3 |  | unimplemented | RW
40563 | Tms12 | 3 |  | unimplemented | RW
40564 | V12 | 3 |  | unimplemented | RW
40565 | Tms13 | 3 |  | unimplemented | RW
40566 | V13 | 3 |  | unimplemented | RW
40567 | Tms14 | 3 |  | unimplemented | RW
40568 | V14 | 3 |  | unimplemented | RW
40569 | Tms15 | 3 |  | unimplemented | RW
40570 | V15 | 3 |  | unimplemented | RW
40571 | Tms16 | 3 |  | unimplemented | RW
40572 | V16 | 3 |  | unimplemented | RW
40573 | Tms17 | 3 |  | unimplemented | RW
40574 | V17 | 3 |  | unimplemented | RW
40575 | Tms18 | 3 |  | unimplemented | RW
40576 | V18 | 3 |  | unimplemented | RW
40577 | Tms19 | 3 |  | unimplemented | RW
40578 | V19 | 3 |  | unimplemented | RW
40579 | Tms20 | 3 |  | unimplemented | RW
40580 | V20 | 3 |  | unimplemented | RW
40581 | CrvNam | 3 |  | unimplemented | RW
40589 | ReadOnly | 3 |  | supported | R
40590 | ActPt | 4 |  | supported | RW
40591 | Tms1 | 4 |  | supported | RW
40592 | V1 | 4 |  | supported | RW
40593 | Tms2 | 4 |  | supported | RW
40594 | V2 | 4 |  | supported | RW
40595 | Tms3 | 4 |  | supported | RW
40596 | V3 | 4 |  | supported | RW
40597 | Tms4 | 4 |  | supported | RW
40598 | V4 | 4 |  | supported | RW
40599 | Tms5 | 4 |  | supported | RW
40600 | V5 | 4 |  | supported | RW
40601 | Tms6 | 4 |  | supported | RW
40602 | V6 | 4 |  | supported | RW
40603 | Tms7 | 4 |  | supported | RW
40604 | V7 | 4 |  | supported | RW
40605 | Tms8 | 4 |  | supported | RW
40606 | V8 | 4 |  | supported | RW
40607 | Tms9 | 4 |  | supported | RW
40608 | V9 | 4 |  | supported | RW
40609 | Tms10 | 4 |  | supported | RW
40610 | V10 | 4 |  | supported | RW
40611 | Tms11 | 4 |  | unimplemented | RW
40612 | V11 | 4 |  | unimplemented | RW
40613 | Tms12 | 4 |  | unimplemented | RW
40614 | V12 | 4 |  | unimplemented | RW
40615 | Tms13 | 4 |  | unimplemented | RW
40616 | V13 | 4 |  | unimplemented | RW
40617 | Tms14 | 4 |  | unimplemented | RW
40618 | V14 | 4 |  | unimplemented | RW
40619 | Tms15 | 4 |  | unimplemented | RW
40620 | V15 | 4 |  | unimplemented | RW
40621 | Tms16 | 4 |  | unimplemented | RW
40622 | V16 | 4 |  | unimplemented | RW
40623 | Tms17 | 4 |  | unimplemented | RW
40624 | V17 | 4 |  | unimplemented | RW
40625 | Tms18 | 4 |  | unimplemented | RW
40626 | V18 | 4 |  | unimplemented | RW
40627 | Tms19 | 4 |  | unimplemented | RW
40628 | V19 | 4 |  | unimplemented | RW
40629 | Tms20 | 4 |  | unimplemented | RW
40630 | V20 | 4 |  | unimplemented | RW
40631 | CrvNam | 4 |  | unimplemented | RW
40639 | ReadOnly | 4 |  | supported | R

## 130
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40640 | ID |  |  | 130
40641 | L |  |  | 210
40642 | ActCrv |  |  | supported | RW
40643 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40644 | WinTms |  |  | unimplemented | RW
40645 | RvrtTms |  |  | unimplemented | RW
40646 | RmpTms |  |  | unimplemented | RW
40647 | NCrv |  |  | supported | R
40648 | NPt |  |  | supported | R
40649 | Tms_SF |  |  | -2 | R
40650 | V_SF |  |  | -1 | R
40651 | Pad |  |  |  | R
40652 | ActPt | 1 |  | supported | RW
40653 | Tms1 | 1 |  | supported | RW
40654 | V1 | 1 |  | supported | RW
40655 | Tms2 | 1 |  | supported | RW
40656 | V2 | 1 |  | supported | RW
40657 | Tms3 | 1 |  | supported | RW
40658 | V3 | 1 |  | supported | RW
40659 | Tms4 | 1 |  | supported | RW
40660 | V4 | 1 |  | supported | RW
40661 | Tms5 | 1 |  | supported | RW
40662 | V5 | 1 |  | supported | RW
40663 | Tms6 | 1 |  | supported | RW
40664 | V6 | 1 |  | supported | RW
40665 | Tms7 | 1 |  | supported | RW
40666 | V7 | 1 |  | supported | RW
40667 | Tms8 | 1 |  | supported | RW
40668 | V8 | 1 |  | supported | RW
40669 | Tms9 | 1 |  | supported | RW
40670 | V9 | 1 |  | supported | RW
40671 | Tms10 | 1 |  | supported | RW
40672 | V10 | 1 |  | supported | RW
40673 | Tms11 | 1 |  | unimplemented | RW
40674 | V11 | 1 |  | unimplemented | RW
40675 | Tms12 | 1 |  | unimplemented | RW
40676 | V12 | 1 |  | unimplemented | RW
40677 | Tms13 | 1 |  | unimplemented | RW
40678 | V13 | 1 |  | unimplemented | RW
40679 | Tms14 | 1 |  | unimplemented | RW
40680 | V14 | 1 |  | unimplemented | RW
40681 | Tms15 | 1 |  | unimplemented | RW
40682 | V15 | 1 |  | unimplemented | RW
40683 | Tms16 | 1 |  | unimplemented | RW
40684 | V16 | 1 |  | unimplemented | RW
40685 | Tms17 | 1 |  | unimplemented | RW
40686 | V17 | 1 |  | unimplemented | RW
40687 | Tms18 | 1 |  | unimplemented | RW
40688 | V18 | 1 |  | unimplemented | RW
40689 | Tms19 | 1 |  | unimplemented | RW
40690 | V19 | 1 |  | unimplemented | RW
40691 | Tms20 | 1 |  | unimplemented | RW
40692 | V20 | 1 |  | unimplemented | RW
40693 | CrvNam | 1 |  | unimplemented | RW
40701 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
40702 | ActPt | 2 |  | supported | RW
40703 | Tms1 | 2 |  | supported | RW
40704 | V1 | 2 |  | supported | RW
40705 | Tms2 | 2 |  | supported | RW
40706 | V2 | 2 |  | supported | RW
40707 | Tms3 | 2 |  | supported | RW
40708 | V3 | 2 |  | supported | RW
40709 | Tms4 | 2 |  | supported | RW
40710 | V4 | 2 |  | supported | RW
40711 | Tms5 | 2 |  | supported | RW
40712 | V5 | 2 |  | supported | RW
40713 | Tms6 | 2 |  | supported | RW
40714 | V6 | 2 |  | supported | RW
40715 | Tms7 | 2 |  | supported | RW
40716 | V7 | 2 |  | supported | RW
40717 | Tms8 | 2 |  | supported | RW
40718 | V8 | 2 |  | supported | RW
40719 | Tms9 | 2 |  | supported | RW
40720 | V9 | 2 |  | supported | RW
40721 | Tms10 | 2 |  | supported | RW
40722 | V10 | 2 |  | supported | RW
40723 | Tms11 | 2 |  | unimplemented | RW
40724 | V11 | 2 |  | unimplemented | RW
40725 | Tms12 | 2 |  | unimplemented | RW
40726 | V12 | 2 |  | unimplemented | RW
40727 | Tms13 | 2 |  | unimplemented | RW
40728 | V13 | 2 |  | unimplemented | RW
40729 | Tms14 | 2 |  | unimplemented | RW
40730 | V14 | 2 |  | unimplemented | RW
40731 | Tms15 | 2 |  | unimplemented | RW
40732 | V15 | 2 |  | unimplemented | RW
40733 | Tms16 | 2 |  | unimplemented | RW
40734 | V16 | 2 |  | unimplemented | RW
40735 | Tms17 | 2 |  | unimplemented | RW
40736 | V17 | 2 |  | unimplemented | RW
40737 | Tms18 | 2 |  | unimplemented | RW
40738 | V18 | 2 |  | unimplemented | RW
40739 | Tms19 | 2 |  | unimplemented | RW
40740 | V19 | 2 |  | unimplemented | RW
40741 | Tms20 | 2 |  | unimplemented | RW
40742 | V20 | 2 |  | unimplemented | RW
40743 | CrvNam | 2 |  | unimplemented | RW
40751 | ReadOnly | 2 |  | supported | R
40752 | ActPt | 3 |  | supported | RW
40753 | Tms1 | 3 |  | supported | RW
40754 | V1 | 3 |  | supported | RW
40755 | Tms2 | 3 |  | supported | RW
40756 | V2 | 3 |  | supported | RW
40757 | Tms3 | 3 |  | supported | RW
40758 | V3 | 3 |  | supported | RW
40759 | Tms4 | 3 |  | supported | RW
40760 | V4 | 3 |  | supported | RW
40761 | Tms5 | 3 |  | supported | RW
40762 | V5 | 3 |  | supported | RW
40763 | Tms6 | 3 |  | supported | RW
40764 | V6 | 3 |  | supported | RW
40765 | Tms7 | 3 |  | supported | RW
40766 | V7 | 3 |  | supported | RW
40767 | Tms8 | 3 |  | supported | RW
40768 | V8 | 3 |  | supported | RW
40769 | Tms9 | 3 |  | supported | RW
40770 | V9 | 3 |  | supported | RW
40771 | Tms10 | 3 |  | supported | RW
40772 | V10 | 3 |  | supported | RW
40773 | Tms11 | 3 |  | unimplemented | RW
40774 | V11 | 3 |  | unimplemented | RW
40775 | Tms12 | 3 |  | unimplemented | RW
40776 | V12 | 3 |  | unimplemented | RW
40777 | Tms13 | 3 |  | unimplemented | RW
40778 | V13 | 3 |  | unimplemented | RW
40779 | Tms14 | 3 |  | unimplemented | RW
40780 | V14 | 3 |  | unimplemented | RW
40781 | Tms15 | 3 |  | unimplemented | RW
40782 | V15 | 3 |  | unimplemented | RW
40783 | Tms16 | 3 |  | unimplemented | RW
40784 | V16 | 3 |  | unimplemented | RW
40785 | Tms17 | 3 |  | unimplemented | RW
40786 | V17 | 3 |  | unimplemented | RW
40787 | Tms18 | 3 |  | unimplemented | RW
40788 | V18 | 3 |  | unimplemented | RW
40789 | Tms19 | 3 |  | unimplemented | RW
40790 | V19 | 3 |  | unimplemented | RW
40791 | Tms20 | 3 |  | unimplemented | RW
40792 | V20 | 3 |  | unimplemented | RW
40793 | CrvNam | 3 |  | unimplemented | RW
40801 | ReadOnly | 3 |  | supported | R
40802 | ActPt | 4 |  | supported | RW
40803 | Tms1 | 4 |  | supported | RW
40804 | V1 | 4 |  | supported | RW
40805 | Tms2 | 4 |  | supported | RW
40806 | V2 | 4 |  | supported | RW
40807 | Tms3 | 4 |  | supported | RW
40808 | V3 | 4 |  | supported | RW
40809 | Tms4 | 4 |  | supported | RW
40810 | V4 | 4 |  | supported | RW
40811 | Tms5 | 4 |  | supported | RW
40812 | V5 | 4 |  | supported | RW
40813 | Tms6 | 4 |  | supported | RW
40814 | V6 | 4 |  | supported | RW
40815 | Tms7 | 4 |  | supported | RW
40816 | V7 | 4 |  | supported | RW
40817 | Tms8 | 4 |  | supported | RW
40818 | V8 | 4 |  | supported | RW
40819 | Tms9 | 4 |  | supported | RW
40820 | V9 | 4 |  | supported | RW
40821 | Tms10 | 4 |  | supported | RW
40822 | V10 | 4 |  | supported | RW
40823 | Tms11 | 4 |  | unimplemented | RW
40824 | V11 | 4 |  | unimplemented | RW
40825 | Tms12 | 4 |  | unimplemented | RW
40826 | V12 | 4 |  | unimplemented | RW
40827 | Tms13 | 4 |  | unimplemented | RW
40828 | V13 | 4 |  | unimplemented | RW
40829 | Tms14 | 4 |  | unimplemented | RW
40830 | V14 | 4 |  | unimplemented | RW
40831 | Tms15 | 4 |  | unimplemented | RW
40832 | V15 | 4 |  | unimplemented | RW
40833 | Tms16 | 4 |  | unimplemented | RW
40834 | V16 | 4 |  | unimplemented | RW
40835 | Tms17 | 4 |  | unimplemented | RW
40836 | V17 | 4 |  | unimplemented | RW
40837 | Tms18 | 4 |  | unimplemented | RW
40838 | V18 | 4 |  | unimplemented | RW
40839 | Tms19 | 4 |  | unimplemented | RW
40840 | V19 | 4 |  | unimplemented | RW
40841 | Tms20 | 4 |  | unimplemented | RW
40842 | V20 | 4 |  | unimplemented | RW
40843 | CrvNam | 4 |  | unimplemented | RW
40851 | ReadOnly | 4 |  | supported | R

## 132
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40852 | ID |  |  | 132
40853 | L |  |  | 226
40854 | ActCrv |  |  | supported | RW
40855 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40856 | WinTms |  |  | unimplemented | RW
40857 | RvrtTms |  |  | unimplemented | RW
40858 | RmpTms |  |  | unimplemented | RW
40859 | NCrv |  |  | supported | R
40860 | NPt |  |  | supported | R
40861 | V_SF |  |  | -1 | R
40862 | DeptRef_SF |  |  | -1 | R
40863 | RmpIncDec_SF |  |  | 0 | R
40864 | ActPt | 1 |  | supported | RW
40865 | DeptRef | 1 |  | supported | RW
|  |  | %WMax | supported
|  |  | %WAval | supported
40866 | V1 | 1 |  | supported | RW
40867 | W1 | 1 |  | supported | RW
40868 | V2 | 1 |  | supported | RW
40869 | W2 | 1 |  | supported | RW
40870 | V3 | 1 |  | supported | RW
40871 | W3 | 1 |  | supported | RW
40872 | V4 | 1 |  | supported | RW
40873 | W4 | 1 |  | supported | RW
40874 | V5 | 1 |  | supported | RW
40875 | W5 | 1 |  | supported | RW
40876 | V6 | 1 |  | supported | RW
40877 | W6 | 1 |  | supported | RW
40878 | V7 | 1 |  | supported | RW
40879 | W7 | 1 |  | supported | RW
40880 | V8 | 1 |  | supported | RW
40881 | W8 | 1 |  | supported | RW
40882 | V9 | 1 |  | supported | RW
40883 | W9 | 1 |  | supported | RW
40884 | V10 | 1 |  | supported | RW
40885 | W10 | 1 |  | supported | RW
40886 | V11 | 1 |  | unimplemented | RW
40887 | W11 | 1 |  | unimplemented | RW
40888 | V12 | 1 |  | unimplemented | RW
40889 | W12 | 1 |  | unimplemented | RW
40890 | V13 | 1 |  | unimplemented | RW
40891 | W13 | 1 |  | unimplemented | RW
40892 | V14 | 1 |  | unimplemented | RW
40893 | W14 | 1 |  | unimplemented | RW
40894 | V15 | 1 |  | unimplemented | RW
40895 | W15 | 1 |  | unimplemented | RW
40896 | V16 | 1 |  | unimplemented | RW
40897 | W16 | 1 |  | unimplemented | RW
40898 | V17 | 1 |  | unimplemented | RW
40899 | W17 | 1 |  | unimplemented | RW
40900 | V18 | 1 |  | unimplemented | RW
40901 | W18 | 1 |  | unimplemented | RW
40902 | V19 | 1 |  | unimplemented | RW
40903 | W19 | 1 |  | unimplemented | RW
40904 | V20 | 1 |  | unimplemented | RW
40905 | W20 | 1 |  | unimplemented | RW
40906 | CrvNam | 1 |  | unimplemented | RW
40914 | RmpPt1Tms | 1 |  | unimplemented | RW
40915 | RmpDecTmm | 1 |  | unimplemented | RW
40916 | RmpIncTmm | 1 |  | unimplemented | RW
40917 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
40918 | ActPt | 2 |  | supported | RW
40919 | DeptRef | 2 |  | supported | RW
40920 | V1 | 2 |  | supported | RW
40921 | W1 | 2 |  | supported | RW
40922 | V2 | 2 |  | supported | RW
40923 | W2 | 2 |  | supported | RW
40924 | V3 | 2 |  | supported | RW
40925 | W3 | 2 |  | supported | RW
40926 | V4 | 2 |  | supported | RW
40927 | W4 | 2 |  | supported | RW
40928 | V5 | 2 |  | supported | RW
40929 | W5 | 2 |  | supported | RW
40930 | V6 | 2 |  | supported | RW
40931 | W6 | 2 |  | supported | RW
40932 | V7 | 2 |  | supported | RW
40933 | W7 | 2 |  | supported | RW
40934 | V8 | 2 |  | supported | RW
40935 | W8 | 2 |  | supported | RW
40936 | V9 | 2 |  | supported | RW
40937 | W9 | 2 |  | supported | RW
40938 | V10 | 2 |  | supported | RW
40939 | W10 | 2 |  | supported | RW
40940 | V11 | 2 |  | unimplemented | RW
40941 | W11 | 2 |  | unimplemented | RW
40942 | V12 | 2 |  | unimplemented | RW
40943 | W12 | 2 |  | unimplemented | RW
40944 | V13 | 2 |  | unimplemented | RW
40945 | W13 | 2 |  | unimplemented | RW
40946 | V14 | 2 |  | unimplemented | RW
40947 | W14 | 2 |  | unimplemented | RW
40948 | V15 | 2 |  | unimplemented | RW
40949 | W15 | 2 |  | unimplemented | RW
40950 | V16 | 2 |  | unimplemented | RW
40951 | W16 | 2 |  | unimplemented | RW
40952 | V17 | 2 |  | unimplemented | RW
40953 | W17 | 2 |  | unimplemented | RW
40954 | V18 | 2 |  | unimplemented | RW
40955 | W18 | 2 |  | unimplemented | RW
40956 | V19 | 2 |  | unimplemented | RW
40957 | W19 | 2 |  | unimplemented | RW
40958 | V20 | 2 |  | unimplemented | RW
40959 | W20 | 2 |  | unimplemented | RW
40960 | CrvNam | 2 |  | unimplemented | RW
40968 | RmpPt1Tms | 2 |  | unimplemented | RW
40969 | RmpDecTmm | 2 |  | unimplemented | RW
40970 | RmpIncTmm | 2 |  | unimplemented | RW
40971 | ReadOnly | 2 |  | supported | R
40972 | ActPt | 3 |  | supported | RW
40973 | DeptRef | 3 |  | supported | RW
40974 | V1 | 3 |  | supported | RW
40975 | W1 | 3 |  | supported | RW
40976 | V2 | 3 |  | supported | RW
40977 | W2 | 3 |  | supported | RW
40978 | V3 | 3 |  | supported | RW
40979 | W3 | 3 |  | supported | RW
40980 | V4 | 3 |  | supported | RW
40981 | W4 | 3 |  | supported | RW
40982 | V5 | 3 |  | supported | RW
40983 | W5 | 3 |  | supported | RW
40984 | V6 | 3 |  | supported | RW
40985 | W6 | 3 |  | supported | RW
40986 | V7 | 3 |  | supported | RW
40987 | W7 | 3 |  | supported | RW
40988 | V8 | 3 |  | supported | RW
40989 | W8 | 3 |  | supported | RW
40990 | V9 | 3 |  | supported | RW
40991 | W9 | 3 |  | supported | RW
40992 | V10 | 3 |  | supported | RW
40993 | W10 | 3 |  | supported | RW
40994 | V11 | 3 |  | unimplemented | RW
40995 | W11 | 3 |  | unimplemented | RW
40996 | V12 | 3 |  | unimplemented | RW
40997 | W12 | 3 |  | unimplemented | RW
40998 | V13 | 3 |  | unimplemented | RW
40999 | W13 | 3 |  | unimplemented | RW
41000 | V14 | 3 |  | unimplemented | RW
41001 | W14 | 3 |  | unimplemented | RW
41002 | V15 | 3 |  | unimplemented | RW
41003 | W15 | 3 |  | unimplemented | RW
41004 | V16 | 3 |  | unimplemented | RW
41005 | W16 | 3 |  | unimplemented | RW
41006 | V17 | 3 |  | unimplemented | RW
41007 | W17 | 3 |  | unimplemented | RW
41008 | V18 | 3 |  | unimplemented | RW
41009 | W18 | 3 |  | unimplemented | RW
41010 | V19 | 3 |  | unimplemented | RW
41011 | W19 | 3 |  | unimplemented | RW
41012 | V20 | 3 |  | unimplemented | RW
41013 | W20 | 3 |  | unimplemented | RW
41014 | CrvNam | 3 |  | unimplemented | RW
41022 | RmpPt1Tms | 3 |  | unimplemented | RW
41023 | RmpDecTmm | 3 |  | unimplemented | RW
41024 | RmpIncTmm | 3 |  | unimplemented | RW
41025 | ReadOnly | 3 |  | supported | R
41026 | ActPt | 4 |  | supported | RW
41027 | DeptRef | 4 |  | supported | RW
41028 | V1 | 4 |  | supported | RW
41029 | W1 | 4 |  | supported | RW
41030 | V2 | 4 |  | supported | RW
41031 | W2 | 4 |  | supported | RW
41032 | V3 | 4 |  | supported | RW
41033 | W3 | 4 |  | supported | RW
41034 | V4 | 4 |  | supported | RW
41035 | W4 | 4 |  | supported | RW
41036 | V5 | 4 |  | supported | RW
41037 | W5 | 4 |  | supported | RW
41038 | V6 | 4 |  | supported | RW
41039 | W6 | 4 |  | supported | RW
41040 | V7 | 4 |  | supported | RW
41041 | W7 | 4 |  | supported | RW
41042 | V8 | 4 |  | supported | RW
41043 | W8 | 4 |  | supported | RW
41044 | V9 | 4 |  | supported | RW
41045 | W9 | 4 |  | supported | RW
41046 | V10 | 4 |  | supported | RW
41047 | W10 | 4 |  | supported | RW
41048 | V11 | 4 |  | unimplemented | RW
41049 | W11 | 4 |  | unimplemented | RW
41050 | V12 | 4 |  | unimplemented | RW
41051 | W12 | 4 |  | unimplemented | RW
41052 | V13 | 4 |  | unimplemented | RW
41053 | W13 | 4 |  | unimplemented | RW
41054 | V14 | 4 |  | unimplemented | RW
41055 | W14 | 4 |  | unimplemented | RW
41056 | V15 | 4 |  | unimplemented | RW
41057 | W15 | 4 |  | unimplemented | RW
41058 | V16 | 4 |  | unimplemented | RW
41059 | W16 | 4 |  | unimplemented | RW
41060 | V17 | 4 |  | unimplemented | RW
41061 | W17 | 4 |  | unimplemented | RW
41062 | V18 | 4 |  | unimplemented | RW
41063 | W18 | 4 |  | unimplemented | RW
41064 | V19 | 4 |  | unimplemented | RW
41065 | W19 | 4 |  | unimplemented | RW
41066 | V20 | 4 |  | unimplemented | RW
41067 | W20 | 4 |  | unimplemented | RW
41068 | CrvNam | 4 |  | unimplemented | RW
41076 | RmpPt1Tms | 4 |  | unimplemented | RW
41077 | RmpDecTmm | 4 |  | unimplemented | RW
41078 | RmpIncTmm | 4 |  | unimplemented | RW
41079 | ReadOnly | 4 |  | supported | R

## 134
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
41080 | ID |  |  | 134
41081 | L |  |  | 242
41082 | ActCrv |  |  | supported | RW
41083 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
41084 | WinTms |  |  | unimplemented | RW
41085 | RvrtTms |  |  | unimplemented | RW
41086 | RmpTms |  |  | unimplemented | RW
41087 | NCrv |  |  | supported | R
41088 | NPt |  |  | supported | R
41089 | Hz_SF |  |  | -2 | R
41090 | W_SF |  |  | -1 | R
41091 | RmpIncDec_SF |  |  | 0 | R
41092 | ActPt | 1 |  | supported | RW
41093 | Hz1 | 1 |  | supported | RW
41094 | W1 | 1 |  | supported | RW
41095 | Hz2 | 1 |  | supported | RW
41096 | W2 | 1 |  | supported | RW
41097 | Hz3 | 1 |  | supported | RW
41098 | W3 | 1 |  | supported | RW
41099 | Hz4 | 1 |  | supported | RW
41100 | W4 | 1 |  | supported | RW
41101 | Hz5 | 1 |  | supported | RW
41102 | W5 | 1 |  | supported | RW
41103 | Hz6 | 1 |  | supported | RW
41104 | W6 | 1 |  | supported | RW
41105 | Hz7 | 1 |  | supported | RW
41106 | W7 | 1 |  | supported | RW
41107 | Hz8 | 1 |  | supported | RW
41108 | W8 | 1 |  | supported | RW
41109 | Hz9 | 1 |  | supported | RW
41110 | W9 | 1 |  | supported | RW
41111 | Hz10 | 1 |  | supported | RW
41112 | W10 | 1 |  | supported | RW
41113 | Hz11 | 1 |  | unimplemented | RW
41114 | W11 | 1 |  | unimplemented | RW
41115 | Hz12 | 1 |  | unimplemented | RW
41116 | W12 | 1 |  | unimplemented | RW
41117 | Hz13 | 1 |  | unimplemented | RW
41118 | W13 | 1 |  | unimplemented | RW
41119 | Hz14 | 1 |  | unimplemented | RW
41120 | W14 | 1 |  | unimplemented | RW
41121 | Hz15 | 1 |  | unimplemented | RW
41122 | W15 | 1 |  | unimplemented | RW
41123 | Hz16 | 1 |  | unimplemented | RW
41124 | W16 | 1 |  | unimplemented | RW
41125 | Hz17 | 1 |  | unimplemented | RW
41126 | W17 | 1 |  | unimplemented | RW
41127 | Hz18 | 1 |  | unimplemented | RW
41128 | W18 | 1 |  | unimplemented | RW
41129 | Hz19 | 1 |  | unimplemented | RW
41130 | W19 | 1 |  | unimplemented | RW
41131 | Hz20 | 1 |  | unimplemented | RW
41132 | W20 | 1 |  | unimplemented | RW
41133 | CrvNam | 1 |  | unimplemented | RW
41141 | RmpPT1Tms | 1 |  | unimplemented | RW
41142 | RmpDecTmm | 1 |  | unimplemented | RW
41143 | RmpIncTmm | 1 |  | unimplemented | RW
41144 | RmpRsUp | 1 |  | unimplemented | RW
41145 | SnptW | 1 |  | unimplemented | RW
41146 | WRef | 1 |  | unimplemented | RW
41147 | WRefStrHz | 1 |  | unimplemented | RW
41148 | WRefStopHz | 1 |  | unimplemented | RW
41149 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
41150 | ActPt | 2 |  | supported | RW
41151 | Hz1 | 2 |  | supported | RW
41152 | W1 | 2 |  | supported | RW
41153 | Hz2 | 2 |  | supported | RW
41154 | W2 | 2 |  | supported | RW
41155 | Hz3 | 2 |  | supported | RW
41156 | W3 | 2 |  | supported | RW
41157 | Hz4 | 2 |  | supported | RW
41158 | W4 | 2 |  | supported | RW
41159 | Hz5 | 2 |  | supported | RW
41160 | W5 | 2 |  | supported | RW
41161 | Hz6 | 2 |  | supported | RW
41162 | W6 | 2 |  | supported | RW
41163 | Hz7 | 2 |  | supported | RW
41164 | W7 | 2 |  | supported | RW
41165 | Hz8 | 2 |  | supported | RW
41166 | W8 | 2 |  | supported | RW
41167 | Hz9 | 2 |  | supported | RW
41168 | W9 | 2 |  | supported | RW
41169 | Hz10 | 2 |  | supported | RW
41170 | W10 | 2 |  | supported | RW
41171 | Hz11 | 2 |  | unimplemented | RW
41172 | W11 | 2 |  | unimplemented | RW
41173 | Hz12 | 2 |  | unimplemented | RW
41174 | W12 | 2 |  | unimplemented | RW
41175 | Hz13 | 2 |  | unimplemented | RW
41176 | W13 | 2 |  | unimplemented | RW
41177 | Hz14 | 2 |  | unimplemented | RW
41178 | W14 | 2 |  | unimplemented | RW
41179 | Hz15 | 2 |  | unimplemented | RW
41180 | W15 | 2 |  | unimplemented | RW
41181 | Hz16 | 2 |  | unimplemented | RW
41182 | W16 | 2 |  | unimplemented | RW
41183 | Hz17 | 2 |  | unimplemented | RW
41184 | W17 | 2 |  | unimplemented | RW
41185 | Hz18 | 2 |  | unimplemented | RW
41186 | W18 | 2 |  | unimplemented | RW
41187 | Hz19 | 2 |  | unimplemented | RW
41188 | W19 | 2 |  | unimplemented | RW
41189 | Hz20 | 2 |  | unimplemented | RW
41190 | W20 | 2 |  | unimplemented | RW
41191 | CrvNam | 2 |  | unimplemented | RW
41199 | RmpPT1Tms | 2 |  | unimplemented | RW
41200 | RmpDecTmm | 2 |  | unimplemented | RW
41201 | RmpIncTmm | 2 |  | unimplemented | RW
41202 | RmpRsUp | 2 |  | unimplemented | RW
41203 | SnptW | 2 |  | unimplemented | RW
41204 | WRef | 2 |  | unimplemented | RW
41205 | WRefStrHz | 2 |  | unimplemented | RW
41206 | WRefStopHz | 2 |  | unimplemented | RW
41207 | ReadOnly | 2 |  | supported | R
41208 | ActPt | 3 |  | supported | RW
41209 | Hz1 | 3 |  | supported | RW
41210 | W1 | 3 |  | supported | RW
41211 | Hz2 | 3 |  | supported | RW
41212 | W2 | 3 |  | supported | RW
41213 | Hz3 | 3 |  | supported | RW
41214 | W3 | 3 |  | supported | RW
41215 | Hz4 | 3 |  | supported | RW
41216 | W4 | 3 |  | supported | RW
41217 | Hz5 | 3 |  | supported | RW
41218 | W5 | 3 |  | supported | RW
41219 | Hz6 | 3 |  | supported | RW
41220 | W6 | 3 |  | supported | RW
41221 | Hz7 | 3 |  | supported | RW
41222 | W7 | 3 |  | supported | RW
41223 | Hz8 | 3 |  | supported | RW
41224 | W8 | 3 |  | supported | RW
41225 | Hz9 | 3 |  | supported | RW
41226 | W9 | 3 |  | supported | RW
41227 | Hz10 | 3 |  | supported | RW
41228 | W10 | 3 |  | supported | RW
41229 | Hz11 | 3 |  | unimplemented | RW
41230 | W11 | 3 |  | unimplemented | RW
41231 | Hz12 | 3 |  | unimplemented | RW
41232 | W12 | 3 |  | unimplemented | RW
41233 | Hz13 | 3 |  | unimplemented | RW
41234 | W13 | 3 |  | unimplemented | RW
41235 | Hz14 | 3 |  | unimplemented | RW
41236 | W14 | 3 |  | unimplemented | RW
41237 | Hz15 | 3 |  | unimplemented | RW
41238 | W15 | 3 |  | unimplemented | RW
41239 | Hz16 | 3 |  | unimplemented | RW
41240 | W16 | 3 |  | unimplemented | RW
41241 | Hz17 | 3 |  | unimplemented | RW
41242 | W17 | 3 |  | unimplemented | RW
41243 | Hz18 | 3 |  | unimplemented | RW
41244 | W18 | 3 |  | unimplemented | RW
41245 | Hz19 | 3 |  | unimplemented | RW
41246 | W19 | 3 |  | unimplemented | RW
41247 | Hz20 | 3 |  | unimplemented | RW
41248 | W20 | 3 |  | unimplemented | RW
41249 | CrvNam | 3 |  | unimplemented | RW
41257 | RmpPT1Tms | 3 |  | unimplemented | RW
41258 | RmpDecTmm | 3 |  | unimplemented | RW
41259 | RmpIncTmm | 3 |  | unimplemented | RW
41260 | RmpRsUp | 3 |  | unimplemented | RW
41261 | SnptW | 3 |  | unimplemented | RW
41262 | WRef | 3 |  | unimplemented | RW
41263 | WRefStrHz | 3 |  | unimplemented | RW
41264 | WRefStopHz | 3 |  | unimplemented | RW
41265 | ReadOnly | 3 |  | supported | R
41266 | ActPt | 4 |  | supported | RW
41267 | Hz1 | 4 |  | supported | RW
41268 | W1 | 4 |  | supported | RW
41269 | Hz2 | 4 |  | supported | RW
41270 | W2 | 4 |  | supported | RW
41271 | Hz3 | 4 |  | supported | RW
41272 | W3 | 4 |  | supported | RW
41273 | Hz4 | 4 |  | supported | RW
41274 | W4 | 4 |  | supported | RW
41275 | Hz5 | 4 |  | supported | RW
41276 | W5 | 4 |  | supported | RW
41277 | Hz6 | 4 |  | supported | RW
41278 | W6 | 4 |  | supported | RW
41279 | Hz7 | 4 |  | supported | RW
41280 | W7 | 4 |  | supported | RW
41281 | Hz8 | 4 |  | supported | RW
41282 | W8 | 4 |  | supported | RW
41283 | Hz9 | 4 |  | supported | RW
41284 | W9 | 4 |  | supported | RW
41285 | Hz10 | 4 |  | supported | RW
41286 | W10 | 4 |  | supported | RW
41287 | Hz11 | 4 |  | unimplemented | RW
41288 | W11 | 4 |  | unimplemented | RW
41289 | Hz12 | 4 |  | unimplemented | RW
41290 | W12 | 4 |  | unimplemented | RW
41291 | Hz13 | 4 |  | unimplemented | RW
41292 | W13 | 4 |  | unimplemented | RW
41293 | Hz14 | 4 |  | unimplemented | RW
41294 | W14 | 4 |  | unimplemented | RW
41295 | Hz15 | 4 |  | unimplemented | RW
41296 | W15 | 4 |  | unimplemented | RW
41297 | Hz16 | 4 |  | unimplemented | RW
41298 | W16 | 4 |  | unimplemented | RW
41299 | Hz17 | 4 |  | unimplemented | RW
41300 | W17 | 4 |  | unimplemented | RW
41301 | Hz18 | 4 |  | unimplemented | RW
41302 | W18 | 4 |  | unimplemented | RW
41303 | Hz19 | 4 |  | unimplemented | RW
41304 | W19 | 4 |  | unimplemented | RW
41305 | Hz20 | 4 |  | unimplemented | RW
41306 | W20 | 4 |  | unimplemented | RW
41307 | CrvNam | 4 |  | unimplemented | RW
41315 | RmpPT1Tms | 4 |  | unimplemented | RW
41316 | RmpDecTmm | 4 |  | unimplemented | RW
41317 | RmpIncTmm | 4 |  | unimplemented | RW
41318 | RmpRsUp | 4 |  | unimplemented | RW
41319 | SnptW | 4 |  | unimplemented | RW
41320 | WRef | 4 |  | unimplemented | RW
41321 | WRefStrHz | 4 |  | unimplemented | RW
41322 | WRefStopHz | 4 |  | unimplemented | RW
41323 | ReadOnly | 4 |  | supported | R

## 64235
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
41324 | ID |  |  | 64235
41325 | L |  |  | 370
41326 | ActCrv |  |  | supported | RW
41327 | ModEna |  |  | unimplemented | RW
|  |  | ENABLED | supported
41328 | WinTms |  |  | unimplemented | RW
41329 | RvrtTms |  |  | unimplemented | RW
41330 | RmpTms |  |  | unimplemented | RW
41331 | NCrv |  |  | supported | R
41332 | NPt |  |  | supported | R
41333 | Tms_SF |  |  | -6 | R
41334 | Hz_SF |  |  | -2 | R
41335 | Pad |  |  |  | R
41336 | ActPt | 1 |  | supported | RW
41337 | Tms1 | 1 |  | supported | RW
41339 | Hz1 | 1 |  | supported | RW
41340 | Fn1 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41341 | Tms2 | 1 |  | supported | RW
41343 | Hz2 | 1 |  | supported | RW
41344 | Fn2 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41345 | Tms3 | 1 |  | supported | RW
41347 | Hz3 | 1 |  | supported | RW
41348 | Fn3 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41349 | Tms4 | 1 |  | supported | RW
41351 | Hz4 | 1 |  | supported | RW
41352 | Fn4 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41353 | Tms5 | 1 |  | supported | RW
41355 | Hz5 | 1 |  | supported | RW
41356 | Fn5 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41357 | Tms6 | 1 |  | supported | RW
41359 | Hz6 | 1 |  | supported | RW
41360 | Fn6 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41361 | Tms7 | 1 |  | supported | RW
41363 | Hz7 | 1 |  | supported | RW
41364 | Fn7 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41365 | Tms8 | 1 |  | supported | RW
41367 | Hz8 | 1 |  | unimplemented | RW
41368 | Fn8 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41369 | Tms9 | 1 |  | unimplemented | RW
41371 | Hz9 | 1 |  | unimplemented | RW
41372 | Fn9 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41373 | Tms10 | 1 |  | unimplemented | RW
41375 | Hz10 | 1 |  | unimplemented | RW
41376 | Fn10 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41377 | Tms11 | 1 |  | unimplemented | RW
41379 | Hz11 | 1 |  | unimplemented | RW
41380 | Fn11 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41381 | Tms12 | 1 |  | unimplemented | RW
41383 | Hz12 | 1 |  | unimplemented | RW
41384 | Fn12 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41385 | Tms13 | 1 |  | unimplemented | RW
41387 | Hz13 | 1 |  | unimplemented | RW
41388 | Fn13 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41389 | Tms14 | 1 |  | unimplemented | RW
41391 | Hz14 | 1 |  | unimplemented | RW
41392 | Fn14 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41393 | Tms15 | 1 |  | unimplemented | RW
41395 | Hz15 | 1 |  | unimplemented | RW
41396 | Fn15 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41397 | Tms16 | 1 |  | unimplemented | RW
41399 | Hz16 | 1 |  | unimplemented | RW
41400 | Fn16 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41401 | Tms17 | 1 |  | unimplemented | RW
41403 | Hz17 | 1 |  | unimplemented | RW
41404 | Fn17 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41405 | Tms18 | 1 |  | unimplemented | RW
41407 | Hz18 | 1 |  | unimplemented | RW
41408 | Fn18 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41409 | Tms19 | 1 |  | unimplemented | RW
41411 | Hz19 | 1 |  | unimplemented | RW
41412 | Fn19 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41413 | Tms20 | 1 |  | unimplemented | RW
41415 | Hz20 | 1 |  | unimplemented | RW
41416 | Fn20 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41417 | CrvNam | 1 |  | unimplemented | RW
41425 | ReadOnly | 1 |  | unimplemented | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
41426 | ActPt | 2 |  | supported | RW
41427 | Tms1 | 2 |  | supported | RW
41429 | Hz1 | 2 |  | supported | RW
41430 | Fn1 | 2 |  | supported | RW
41431 | Tms2 | 2 |  | supported | RW
41433 | Hz2 | 2 |  | supported | RW
41434 | Fn2 | 2 |  | supported | RW
41435 | Tms3 | 2 |  | supported | RW
41437 | Hz3 | 2 |  | supported | RW
41438 | Fn3 | 2 |  | supported | RW
41439 | Tms4 | 2 |  | supported | RW
41441 | Hz4 | 2 |  | supported | RW
41442 | Fn4 | 2 |  | supported | RW
41443 | Tms5 | 2 |  | supported | RW
41445 | Hz5 | 2 |  | supported | RW
41446 | Fn5 | 2 |  | supported | RW
41447 | Tms6 | 2 |  | supported | RW
41449 | Hz6 | 2 |  | supported | RW
41450 | Fn6 | 2 |  | supported | RW
41451 | Tms7 | 2 |  | supported | RW
41453 | Hz7 | 2 |  | supported | RW
41454 | Fn7 | 2 |  | supported | RW
41455 | Tms8 | 2 |  | supported | RW
41457 | Hz8 | 2 |  | unimplemented | RW
41458 | Fn8 | 2 |  | unimplemented | RW
41459 | Tms9 | 2 |  | unimplemented | RW
41461 | Hz9 | 2 |  | unimplemented | RW
41462 | Fn9 | 2 |  | unimplemented | RW
41463 | Tms10 | 2 |  | unimplemented | RW
41465 | Hz10 | 2 |  | unimplemented | RW
41466 | Fn10 | 2 |  | unimplemented | RW
41467 | Tms11 | 2 |  | unimplemented | RW
41469 | Hz11 | 2 |  | unimplemented | RW
41470 | Fn11 | 2 |  | unimplemented | RW
41471 | Tms12 | 2 |  | unimplemented | RW
41473 | Hz12 | 2 |  | unimplemented | RW
41474 | Fn12 | 2 |  | unimplemented | RW
41475 | Tms13 | 2 |  | unimplemented | RW
41477 | Hz13 | 2 |  | unimplemented | RW
41478 | Fn13 | 2 |  | unimplemented | RW
41479 | Tms14 | 2 |  | unimplemented | RW
41481 | Hz14 | 2 |  | unimplemented | RW
41482 | Fn14 | 2 |  | unimplemented | RW
41483 | Tms15 | 2 |  | unimplemented | RW
41485 | Hz15 | 2 |  | unimplemented | RW
41486 | Fn15 | 2 |  | unimplemented | RW
41487 | Tms16 | 2 |  | unimplemented | RW
41489 | Hz16 | 2 |  | unimplemented | RW
41490 | Fn16 | 2 |  | unimplemented | RW
41491 | Tms17 | 2 |  | unimplemented | RW
41493 | Hz17 | 2 |  | unimplemented | RW
41494 | Fn17 | 2 |  | unimplemented | RW
41495 | Tms18 | 2 |  | unimplemented | RW
41497 | Hz18 | 2 |  | unimplemented | RW
41498 | Fn18 | 2 |  | unimplemented | RW
41499 | Tms19 | 2 |  | unimplemented | RW
41501 | Hz19 | 2 |  | unimplemented | RW
41502 | Fn19 | 2 |  | unimplemented | RW
41503 | Tms20 | 2 |  | unimplemented | RW
41505 | Hz20 | 2 |  | unimplemented | RW
41506 | Fn20 | 2 |  | unimplemented | RW
41507 | CrvNam | 2 |  | unimplemented | RW
41515 | ReadOnly | 2 |  | unimplemented | R
41516 | ActPt | 3 |  | supported | RW
41517 | Tms1 | 3 |  | supported | RW
41519 | Hz1 | 3 |  | supported | RW
41520 | Fn1 | 3 |  | supported | RW
41521 | Tms2 | 3 |  | supported | RW
41523 | Hz2 | 3 |  | supported | RW
41524 | Fn2 | 3 |  | supported | RW
41525 | Tms3 | 3 |  | supported | RW
41527 | Hz3 | 3 |  | supported | RW
41528 | Fn3 | 3 |  | supported | RW
41529 | Tms4 | 3 |  | supported | RW
41531 | Hz4 | 3 |  | supported | RW
41532 | Fn4 | 3 |  | supported | RW
41533 | Tms5 | 3 |  | supported | RW
41535 | Hz5 | 3 |  | supported | RW
41536 | Fn5 | 3 |  | supported | RW
41537 | Tms6 | 3 |  | supported | RW
41539 | Hz6 | 3 |  | supported | RW
41540 | Fn6 | 3 |  | supported | RW
41541 | Tms7 | 3 |  | supported | RW
41543 | Hz7 | 3 |  | supported | RW
41544 | Fn7 | 3 |  | supported | RW
41545 | Tms8 | 3 |  | supported | RW
41547 | Hz8 | 3 |  | unimplemented | RW
41548 | Fn8 | 3 |  | unimplemented | RW
41549 | Tms9 | 3 |  | unimplemented | RW
41551 | Hz9 | 3 |  | unimplemented | RW
41552 | Fn9 | 3 |  | unimplemented | RW
41553 | Tms10 | 3 |  | unimplemented | RW
41555 | Hz10 | 3 |  | unimplemented | RW
41556 | Fn10 | 3 |  | unimplemented | RW
41557 | Tms11 | 3 |  | unimplemented | RW
41559 | Hz11 | 3 |  | unimplemented | RW
41560 | Fn11 | 3 |  | unimplemented | RW
41561 | Tms12 | 3 |  | unimplemented | RW
41563 | Hz12 | 3 |  | unimplemented | RW
41564 | Fn12 | 3 |  | unimplemented | RW
41565 | Tms13 | 3 |  | unimplemented | RW
41567 | Hz13 | 3 |  | unimplemented | RW
41568 | Fn13 | 3 |  | unimplemented | RW
41569 | Tms14 | 3 |  | unimplemented | RW
41571 | Hz14 | 3 |  | unimplemented | RW
41572 | Fn14 | 3 |  | unimplemented | RW
41573 | Tms15 | 3 |  | unimplemented | RW
41575 | Hz15 | 3 |  | unimplemented | RW
41576 | Fn15 | 3 |  | unimplemented | RW
41577 | Tms16 | 3 |  | unimplemented | RW
41579 | Hz16 | 3 |  | unimplemented | RW
41580 | Fn16 | 3 |  | unimplemented | RW
41581 | Tms17 | 3 |  | unimplemented | RW
41583 | Hz17 | 3 |  | unimplemented | RW
41584 | Fn17 | 3 |  | unimplemented | RW
41585 | Tms18 | 3 |  | unimplemented | RW
41587 | Hz18 | 3 |  | unimplemented | RW
41588 | Fn18 | 3 |  | unimplemented | RW
41589 | Tms19 | 3 |  | unimplemented | RW
41591 | Hz19 | 3 |  | unimplemented | RW
41592 | Fn19 | 3 |  | unimplemented | RW
41593 | Tms20 | 3 |  | unimplemented | RW
41595 | Hz20 | 3 |  | unimplemented | RW
41596 | Fn20 | 3 |  | unimplemented | RW
41597 | CrvNam | 3 |  | unimplemented | RW
41605 | ReadOnly | 3 |  | unimplemented | R
41606 | ActPt | 4 |  | supported | RW
41607 | Tms1 | 4 |  | supported | RW
41609 | Hz1 | 4 |  | supported | RW
41610 | Fn1 | 4 |  | supported | RW
41611 | Tms2 | 4 |  | supported | RW
41613 | Hz2 | 4 |  | supported | RW
41614 | Fn2 | 4 |  | supported | RW
41615 | Tms3 | 4 |  | supported | RW
41617 | Hz3 | 4 |  | supported | RW
41618 | Fn3 | 4 |  | supported | RW
41619 | Tms4 | 4 |  | supported | RW
41621 | Hz4 | 4 |  | supported | RW
41622 | Fn4 | 4 |  | supported | RW
41623 | Tms5 | 4 |  | supported | RW
41625 | Hz5 | 4 |  | supported | RW
41626 | Fn5 | 4 |  | supported | RW
41627 | Tms6 | 4 |  | supported | RW
41629 | Hz6 | 4 |  | supported | RW
41630 | Fn6 | 4 |  | supported | RW
41631 | Tms7 | 4 |  | supported | RW
41633 | Hz7 | 4 |  | supported | RW
41634 | Fn7 | 4 |  | supported | RW
41635 | Tms8 | 4 |  | supported | RW
41637 | Hz8 | 4 |  | unimplemented | RW
41638 | Fn8 | 4 |  | unimplemented | RW
41639 | Tms9 | 4 |  | unimplemented | RW
41641 | Hz9 | 4 |  | unimplemented | RW
41642 | Fn9 | 4 |  | unimplemented | RW
41643 | Tms10 | 4 |  | unimplemented | RW
41645 | Hz10 | 4 |  | unimplemented | RW
41646 | Fn10 | 4 |  | unimplemented | RW
41647 | Tms11 | 4 |  | unimplemented | RW
41649 | Hz11 | 4 |  | unimplemented | RW
41650 | Fn11 | 4 |  | unimplemented | RW
41651 | Tms12 | 4 |  | unimplemented | RW
41653 | Hz12 | 4 |  | unimplemented | RW
41654 | Fn12 | 4 |  | unimplemented | RW
41655 | Tms13 | 4 |  | unimplemented | RW
41657 | Hz13 | 4 |  | unimplemented | RW
41658 | Fn13 | 4 |  | unimplemented | RW
41659 | Tms14 | 4 |  | unimplemented | RW
41661 | Hz14 | 4 |  | unimplemented | RW
41662 | Fn14 | 4 |  | unimplemented | RW
41663 | Tms15 | 4 |  | unimplemented | RW
41665 | Hz15 | 4 |  | unimplemented | RW
41666 | Fn15 | 4 |  | unimplemented | RW
41667 | Tms16 | 4 |  | unimplemented | RW
41669 | Hz16 | 4 |  | unimplemented | RW
41670 | Fn16 | 4 |  | unimplemented | RW
41671 | Tms17 | 4 |  | unimplemented | RW
41673 | Hz17 | 4 |  | unimplemented | RW
41674 | Fn17 | 4 |  | unimplemented | RW
41675 | Tms18 | 4 |  | unimplemented | RW
41677 | Hz18 | 4 |  | unimplemented | RW
41678 | Fn18 | 4 |  | unimplemented | RW
41679 | Tms19 | 4 |  | unimplemented | RW
41681 | Hz19 | 4 |  | unimplemented | RW
41682 | Fn19 | 4 |  | unimplemented | RW
41683 | Tms20 | 4 |  | unimplemented | RW
41685 | Hz20 | 4 |  | unimplemented | RW
41686 | Fn20 | 4 |  | unimplemented | RW
41687 | CrvNam | 4 |  | unimplemented | RW
41695 | ReadOnly | 4 |  | unimplemented | R

## 64236
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
41696 | ID |  |  | 64236
41697 | L |  |  | 370
41698 | ActCrv |  |  | supported | RW
41699 | ModEna |  |  | unimplemented | RW
|  |  | ENABLED | supported
41700 | WinTms |  |  | unimplemented | RW
41701 | RvrtTms |  |  | unimplemented | RW
41702 | RmpTms |  |  | unimplemented | RW
41703 | NCrv |  |  | supported | R
41704 | NPt |  |  | supported | R
41705 | Tms_SF |  |  | -6 | R
41706 | Hz_SF |  |  | -2 | R
41707 | Pad |  |  |  | R
41708 | ActPt | 1 |  | supported | RW
41709 | Tms1 | 1 |  | supported | RW
41711 | Hz1 | 1 |  | supported | RW
41712 | Fn1 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41713 | Tms2 | 1 |  | supported | RW
41715 | Hz2 | 1 |  | supported | RW
41716 | Fn2 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41717 | Tms3 | 1 |  | supported | RW
41719 | Hz3 | 1 |  | supported | RW
41720 | Fn3 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41721 | Tms4 | 1 |  | supported | RW
41723 | Hz4 | 1 |  | supported | RW
41724 | Fn4 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41725 | Tms5 | 1 |  | supported | RW
41727 | Hz5 | 1 |  | supported | RW
41728 | Fn5 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41729 | Tms6 | 1 |  | supported | RW
41731 | Hz6 | 1 |  | supported | RW
41732 | Fn6 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41733 | Tms7 | 1 |  | supported | RW
41735 | Hz7 | 1 |  | supported | RW
41736 | Fn7 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41737 | Tms8 | 1 |  | supported | RW
41739 | Hz8 | 1 |  | unimplemented | RW
41740 | Fn8 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41741 | Tms9 | 1 |  | unimplemented | RW
41743 | Hz9 | 1 |  | unimplemented | RW
41744 | Fn9 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41745 | Tms10 | 1 |  | unimplemented | RW
41747 | Hz10 | 1 |  | unimplemented | RW
41748 | Fn10 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41749 | Tms11 | 1 |  | unimplemented | RW
41751 | Hz11 | 1 |  | unimplemented | RW
41752 | Fn11 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41753 | Tms12 | 1 |  | unimplemented | RW
41755 | Hz12 | 1 |  | unimplemented | RW
41756 | Fn12 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41757 | Tms13 | 1 |  | unimplemented | RW
41759 | Hz13 | 1 |  | unimplemented | RW
41760 | Fn13 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41761 | Tms14 | 1 |  | unimplemented | RW
41763 | Hz14 | 1 |  | unimplemented | RW
41764 | Fn14 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41765 | Tms15 | 1 |  | unimplemented | RW
41767 | Hz15 | 1 |  | unimplemented | RW
41768 | Fn15 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41769 | Tms16 | 1 |  | unimplemented | RW
41771 | Hz16 | 1 |  | unimplemented | RW
41772 | Fn16 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41773 | Tms17 | 1 |  | unimplemented | RW
41775 | Hz17 | 1 |  | unimplemented | RW
41776 | Fn17 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41777 | Tms18 | 1 |  | unimplemented | RW
41779 | Hz18 | 1 |  | unimplemented | RW
41780 | Fn18 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41781 | Tms19 | 1 |  | unimplemented | RW
41783 | Hz19 | 1 |  | unimplemented | RW
41784 | Fn19 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41785 | Tms20 | 1 |  | unimplemented | RW
41787 | Hz20 | 1 |  | unimplemented | RW
41788 | Fn20 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41789 | CrvNam | 1 |  | unimplemented | RW
41797 | ReadOnly | 1 |  | unimplemented | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
41798 | ActPt | 2 |  | supported | RW
41799 | Tms1 | 2 |  | supported | RW
41801 | Hz1 | 2 |  | supported | RW
41802 | Fn1 | 2 |  | supported | RW
41803 | Tms2 | 2 |  | supported | RW
41805 | Hz2 | 2 |  | supported | RW
41806 | Fn2 | 2 |  | supported | RW
41807 | Tms3 | 2 |  | supported | RW
41809 | Hz3 | 2 |  | supported | RW
41810 | Fn3 | 2 |  | supported | RW
41811 | Tms4 | 2 |  | supported | RW
41813 | Hz4 | 2 |  | supported | RW
41814 | Fn4 | 2 |  | supported | RW
41815 | Tms5 | 2 |  | supported | RW
41817 | Hz5 | 2 |  | supported | RW
41818 | Fn5 | 2 |  | supported | RW
41819 | Tms6 | 2 |  | supported | RW
41821 | Hz6 | 2 |  | supported | RW
41822 | Fn6 | 2 |  | supported | RW
41823 | Tms7 | 2 |  | supported | RW
41825 | Hz7 | 2 |  | supported | RW
41826 | Fn7 | 2 |  | supported | RW
41827 | Tms8 | 2 |  | supported | RW
41829 | Hz8 | 2 |  | unimplemented | RW
41830 | Fn8 | 2 |  | unimplemented | RW
41831 | Tms9 | 2 |  | unimplemented | RW
41833 | Hz9 | 2 |  | unimplemented | RW
41834 | Fn9 | 2 |  | unimplemented | RW
41835 | Tms10 | 2 |  | unimplemented | RW
41837 | Hz10 | 2 |  | unimplemented | RW
41838 | Fn10 | 2 |  | unimplemented | RW
41839 | Tms11 | 2 |  | unimplemented | RW
41841 | Hz11 | 2 |  | unimplemented | RW
41842 | Fn11 | 2 |  | unimplemented | RW
41843 | Tms12 | 2 |  | unimplemented | RW
41845 | Hz12 | 2 |  | unimplemented | RW
41846 | Fn12 | 2 |  | unimplemented | RW
41847 | Tms13 | 2 |  | unimplemented | RW
41849 | Hz13 | 2 |  | unimplemented | RW
41850 | Fn13 | 2 |  | unimplemented | RW
41851 | Tms14 | 2 |  | unimplemented | RW
41853 | Hz14 | 2 |  | unimplemented | RW
41854 | Fn14 | 2 |  | unimplemented | RW
41855 | Tms15 | 2 |  | unimplemented | RW
41857 | Hz15 | 2 |  | unimplemented | RW
41858 | Fn15 | 2 |  | unimplemented | RW
41859 | Tms16 | 2 |  | unimplemented | RW
41861 | Hz16 | 2 |  | unimplemented | RW
41862 | Fn16 | 2 |  | unimplemented | RW
41863 | Tms17 | 2 |  | unimplemented | RW
41865 | Hz17 | 2 |  | unimplemented | RW
41866 | Fn17 | 2 |  | unimplemented | RW
41867 | Tms18 | 2 |  | unimplemented | RW
41869 | Hz18 | 2 |  | unimplemented | RW
41870 | Fn18 | 2 |  | unimplemented | RW
41871 | Tms19 | 2 |  | unimplemented | RW
41873 | Hz19 | 2 |  | unimplemented | RW
41874 | Fn19 | 2 |  | unimplemented | RW
41875 | Tms20 | 2 |  | unimplemented | RW
41877 | Hz20 | 2 |  | unimplemented | RW
41878 | Fn20 | 2 |  | unimplemented | RW
41879 | CrvNam | 2 |  | unimplemented | RW
41887 | ReadOnly | 2 |  | unimplemented | R
41888 | ActPt | 3 |  | supported | RW
41889 | Tms1 | 3 |  | supported | RW
41891 | Hz1 | 3 |  | supported | RW
41892 | Fn1 | 3 |  | supported | RW
41893 | Tms2 | 3 |  | supported | RW
41895 | Hz2 | 3 |  | supported | RW
41896 | Fn2 | 3 |  | supported | RW
41897 | Tms3 | 3 |  | supported | RW
41899 | Hz3 | 3 |  | supported | RW
41900 | Fn3 | 3 |  | supported | RW
41901 | Tms4 | 3 |  | supported | RW
41903 | Hz4 | 3 |  | supported | RW
41904 | Fn4 | 3 |  | supported | RW
41905 | Tms5 | 3 |  | supported | RW
41907 | Hz5 | 3 |  | supported | RW
41908 | Fn5 | 3 |  | supported | RW
41909 | Tms6 | 3 |  | supported | RW
41911 | Hz6 | 3 |  | supported | RW
41912 | Fn6 | 3 |  | supported | RW
41913 | Tms7 | 3 |  | supported | RW
41915 | Hz7 | 3 |  | supported | RW
41916 | Fn7 | 3 |  | supported | RW
41917 | Tms8 | 3 |  | supported | RW
41919 | Hz8 | 3 |  | unimplemented | RW
41920 | Fn8 | 3 |  | unimplemented | RW
41921 | Tms9 | 3 |  | unimplemented | RW
41923 | Hz9 | 3 |  | unimplemented | RW
41924 | Fn9 | 3 |  | unimplemented | RW
41925 | Tms10 | 3 |  | unimplemented | RW
41927 | Hz10 | 3 |  | unimplemented | RW
41928 | Fn10 | 3 |  | unimplemented | RW
41929 | Tms11 | 3 |  | unimplemented | RW
41931 | Hz11 | 3 |  | unimplemented | RW
41932 | Fn11 | 3 |  | unimplemented | RW
41933 | Tms12 | 3 |  | unimplemented | RW
41935 | Hz12 | 3 |  | unimplemented | RW
41936 | Fn12 | 3 |  | unimplemented | RW
41937 | Tms13 | 3 |  | unimplemented | RW
41939 | Hz13 | 3 |  | unimplemented | RW
41940 | Fn13 | 3 |  | unimplemented | RW
41941 | Tms14 | 3 |  | unimplemented | RW
41943 | Hz14 | 3 |  | unimplemented | RW
41944 | Fn14 | 3 |  | unimplemented | RW
41945 | Tms15 | 3 |  | unimplemented | RW
41947 | Hz15 | 3 |  | unimplemented | RW
41948 | Fn15 | 3 |  | unimplemented | RW
41949 | Tms16 | 3 |  | unimplemented | RW
41951 | Hz16 | 3 |  | unimplemented | RW
41952 | Fn16 | 3 |  | unimplemented | RW
41953 | Tms17 | 3 |  | unimplemented | RW
41955 | Hz17 | 3 |  | unimplemented | RW
41956 | Fn17 | 3 |  | unimplemented | RW
41957 | Tms18 | 3 |  | unimplemented | RW
41959 | Hz18 | 3 |  | unimplemented | RW
41960 | Fn18 | 3 |  | unimplemented | RW
41961 | Tms19 | 3 |  | unimplemented | RW
41963 | Hz19 | 3 |  | unimplemented | RW
41964 | Fn19 | 3 |  | unimplemented | RW
41965 | Tms20 | 3 |  | unimplemented | RW
41967 | Hz20 | 3 |  | unimplemented | RW
41968 | Fn20 | 3 |  | unimplemented | RW
41969 | CrvNam | 3 |  | unimplemented | RW
41977 | ReadOnly | 3 |  | unimplemented | R
41978 | ActPt | 4 |  | supported | RW
41979 | Tms1 | 4 |  | supported | RW
41981 | Hz1 | 4 |  | supported | RW
41982 | Fn1 | 4 |  | supported | RW
41983 | Tms2 | 4 |  | supported | RW
41985 | Hz2 | 4 |  | supported | RW
41986 | Fn2 | 4 |  | supported | RW
41987 | Tms3 | 4 |  | supported | RW
41989 | Hz3 | 4 |  | supported | RW
41990 | Fn3 | 4 |  | supported | RW
41991 | Tms4 | 4 |  | supported | RW
41993 | Hz4 | 4 |  | supported | RW
41994 | Fn4 | 4 |  | supported | RW
41995 | Tms5 | 4 |  | supported | RW
41997 | Hz5 | 4 |  | supported | RW
41998 | Fn5 | 4 |  | supported | RW
41999 | Tms6 | 4 |  | supported | RW
42001 | Hz6 | 4 |  | supported | RW
42002 | Fn6 | 4 |  | supported | RW
42003 | Tms7 | 4 |  | supported | RW
42005 | Hz7 | 4 |  | supported | RW
42006 | Fn7 | 4 |  | supported | RW
42007 | Tms8 | 4 |  | supported | RW
42009 | Hz8 | 4 |  | unimplemented | RW
42010 | Fn8 | 4 |  | unimplemented | RW
42011 | Tms9 | 4 |  | unimplemented | RW
42013 | Hz9 | 4 |  | unimplemented | RW
42014 | Fn9 | 4 |  | unimplemented | RW
42015 | Tms10 | 4 |  | unimplemented | RW
42017 | Hz10 | 4 |  | unimplemented | RW
42018 | Fn10 | 4 |  | unimplemented | RW
42019 | Tms11 | 4 |  | unimplemented | RW
42021 | Hz11 | 4 |  | unimplemented | RW
42022 | Fn11 | 4 |  | unimplemented | RW
42023 | Tms12 | 4 |  | unimplemented | RW
42025 | Hz12 | 4 |  | unimplemented | RW
42026 | Fn12 | 4 |  | unimplemented | RW
42027 | Tms13 | 4 |  | unimplemented | RW
42029 | Hz13 | 4 |  | unimplemented | RW
42030 | Fn13 | 4 |  | unimplemented | RW
42031 | Tms14 | 4 |  | unimplemented | RW
42033 | Hz14 | 4 |  | unimplemented | RW
42034 | Fn14 | 4 |  | unimplemented | RW
42035 | Tms15 | 4 |  | unimplemented | RW
42037 | Hz15 | 4 |  | unimplemented | RW
42038 | Fn15 | 4 |  | unimplemented | RW
42039 | Tms16 | 4 |  | unimplemented | RW
42041 | Hz16 | 4 |  | unimplemented | RW
42042 | Fn16 | 4 |  | unimplemented | RW
42043 | Tms17 | 4 |  | unimplemented | RW
42045 | Hz17 | 4 |  | unimplemented | RW
42046 | Fn17 | 4 |  | unimplemented | RW
42047 | Tms18 | 4 |  | unimplemented | RW
42049 | Hz18 | 4 |  | unimplemented | RW
42050 | Fn18 | 4 |  | unimplemented | RW
42051 | Tms19 | 4 |  | unimplemented | RW
42053 | Hz19 | 4 |  | unimplemented | RW
42054 | Fn19 | 4 |  | unimplemented | RW
42055 | Tms20 | 4 |  | unimplemented | RW
42057 | Hz20 | 4 |  | unimplemented | RW
42058 | Fn20 | 4 |  | unimplemented | RW
42059 | CrvNam | 4 |  | unimplemented | RW
42067 | ReadOnly | 4 |  | unimplemented | R

## 145
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
42068 | ID |  |  | 145
42069 | L |  |  | 8
42070 | Ramp Up Rate (NomRmpUpRte) |  |  | supported | RW
42071 | NomRmpDnRte |  |  | supported | RW
42072 | Emergency Ramp Up Rate (EmgRmpUpRte) |  |  | unimplemented | RW
42073 | Emergency Ramp Down Rate (EmgRmpDnRte) |  |  | unimplemented | RW
42074 | Connect Ramp Up Rate (ConnRmpUpRte) |  |  | supported | RW
42075 | Connect Ramp Down Rate (ConnRmpDnRte) |  |  | unimplemented | RW
42076 | Default Ramp Rate (AGra) |  |  | unimplemented | RW
42077 | Ramp Rate Scale Factor (Rmp_SF) |  |  | -1 | R

## 64203
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
42078 | ID |  |  | 64203
42079 | L |  |  | 12
42080 | ModEna |  |  | supported | RW
|  |  | DISABLE | supported
|  |  | ENABLE | supported
42081 | ReConn_Tms |  |  | supported | RW
42082 | ReConnMinV |  |  | supported | RW
42083 | ReConnMaxV |  |  | supported | RW
42084 | ReConnMinHz |  |  | supported | RW
42085 | ReConnMaxHz |  |  | supported | RW
42086 | VoltWattLatchTime (VWLatchTms) |  |  | supported | RW
42087 | FreqWattLatchTime (FWLatchTms) |  |  | supported | RW
42088 | Tms_SF |  |  | 0 | R
42089 | V_SF |  |  | -1 | R
42090 | Hz_SF |  |  | -2 | R
42091 | Pad |  |  |  | R