## Introduction
SunSpec PICS Template
This SunSpec PICS template was generated by SunSpec Dashboard v1.0.5 based on the model contents of the connected device.
This spreadsheet describes the Modbus mapping for the Pika Energy X7600 series inverter as of 10/24/2017
Please contact Pika Energy before embarking on an integration project to ensure the most up-to-date mapping.

## 1
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40002 | ID |  |  | 1
40003 | L |  |  | 66
40004 | Manufacturer (Mn) |  |  | Pika | R
40020 | Model (Md) |  |  | X7601 Islanding Inverter | R
40036 | Options (Opt) |  |  | unimplemented | R
40044 | Version (Vr) |  |  | 132_11620 | R
40052 | Serial Number (SN) |  |  | 000100070096 | R
40068 | Device Address (DA) |  |  | unimplemented | RW
40069 | Pad |  |  |  | R

## 102
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40070 | ID |  |  | 102
40071 | L |  |  | 50
40072 | Amps (A) |  |  | supported | R
40073 | Amps PhaseA (AphA) |  |  | supported | R
40074 | Amps PhaseB (AphB) |  |  | supported | R
40075 | Amps PhaseC (AphC) |  |  | unimplemented | R
40076 | A_SF |  |  | -2 | R
40077 | Phase Voltage AB (PPVphAB) |  |  | unimplemented | R
40078 | Phase Voltage BC (PPVphBC) |  |  | unimplemented | R
40079 | Phase Voltage CA (PPVphCA) |  |  | unimplemented | R
40080 | Phase Voltage AN (PhVphA) |  |  | supported | R
40081 | Phase Voltage BN (PhVphB) |  |  | supported | R
40082 | Phase Voltage CN (PhVphC) |  |  | unimplemented | R
40083 | V_SF |  |  | -1 | R
40084 | Watts (W) |  |  | supported | R
40085 | W_SF |  |  | 0 | R
40086 | Hz |  |  | supported | R
40087 | Hz_SF |  |  | -2 | R
40088 | VA |  |  | supported | R
40089 | VA_SF |  |  | 0 | R
40090 | VAr |  |  | supported | R
40091 | VAr_SF |  |  | 0 | R
40092 | PF |  |  | supported | R
40093 | PF_SF |  |  | -1 | R
40094 | WattHours (WH) |  |  | supported | R
40096 | WH_SF |  |  | 0 | R
40097 | DC Amps (DCA) |  |  | unimplemented | R
40098 | DCA_SF |  |  | 0 | R
40099 | DC Voltage (DCV) |  |  | supported | R
40100 | DCV_SF |  |  | -1 | R
40101 | DC Watts (DCW) |  |  | unimplemented | R
40102 | DCW_SF |  |  | 0 | R
40103 | Cabinet Temperature (TmpCab) |  |  | supported | R
40104 | Heat Sink Temperature (TmpSnk) |  |  | supported | R
40105 | Transformer Temperature (TmpTrns) |  |  | supported | R
40106 | Other Temperature (TmpOt) |  |  | supported | R
40107 | Tmp_SF |  |  | -1 | R
40108 | Operating State (St) |  |  | supported | R
|  |  | Off (OFF) | supported
|  |  | Sleeping (SLEEPING) | supported
|  |  | Starting (STARTING) | supported
|  |  | MPPT | supported
|  |  | Throttled (THROTTLED) | supported
|  |  | Shutting down (SHUTTING_DOWN) | supported
|  |  | Fault (FAULT) | supported
|  |  | Standby (STANDBY) | supported
40109 | Vendor Operating State (StVnd) |  |  | supported | R
40110 | Event1 (Evt1) |  |  | supported | R
|  |  | Ground fault (GROUND_FAULT) | supported
|  |  | DC over voltage (DC_OVER_VOLT) | supported
|  |  | AC disconnect open (AC_DISCONNECT) | supported
|  |  | DC disconnect open (DC_DISCONNECT) | supported
|  |  | Grid shutdown (GRID_DISCONNECT) | supported
|  |  | Cabinet open (CABINET_OPEN) | supported
|  |  | Manual shutdown (MANUAL_SHUTDOWN) | supported
|  |  | Over temperature (OVER_TEMP) | supported
|  |  | Frequency above limit (OVER_FREQUENCY) | supported
|  |  | Frequency under limit (UNDER_FREQUENCY) | supported
|  |  | AC Voltage above limit (AC_OVER_VOLT) | supported
|  |  | AC Voltage under limit (AC_UNDER_VOLT) | supported
|  |  | Blown String fuse on input (BLOWN_STRING_FUSE) | supported
|  |  | Under temperature (UNDER_TEMP) | supported
|  |  | Generic Memory or Communication error (internal) (MEMORY_LOSS) | supported
|  |  | Hardware test failure (HW_TEST_FAILURE) | supported
40112 | Event Bitfield 2 (Evt2) |  |  | supported | R
40114 | Vendor Event Bitfield 1 (EvtVnd1) |  |  | supported | R
40116 | Vendor Event Bitfield 2 (EvtVnd2) |  |  | supported | R
40118 | Vendor Event Bitfield 3 (EvtVnd3) |  |  | supported | R
40120 | Vendor Event Bitfield 4 (EvtVnd4) |  |  | supported | R

## 64204
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40122 | ID |  |  | 64204
40123 | L |  |  | 8
40124 | Power export line 1 (Px1) |  |  | supported | R
40125 | Power export line 2 (Px2) |  |  | supported | R
40126 | Power export line 3 (Px3) |  |  | supported | R
40127 | Energy exported (Whx) |  |  | supported | R
40129 | Energy imported (Whin) |  |  | supported | R
40131 | Pad |  |  |  | R

## 64202
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40132 | ID |  |  | 64202
40133 | L |  |  | 12
40134 | System Operating Mode (SysMd) |  |  | supported | R
|  |  | SAFETY_SHUTDOWN | supported
|  |  | GRID_CONNECT | supported
|  |  | SELF_SUPPLY | supported
|  |  | CLEAN_BACKUP | supported
|  |  | PRIORITY_BACKUP | supported
|  |  | ARBITRAGE | supported
40135 | Max real power (PMax) |  |  | supported | RW
40136 | Max reactive power (QMax) |  |  | supported | RW
40137 | Real power target (PMaxLimPct) |  |  | supported | RW
40138 | Reactive power target (QMaxLimPct) |  |  | supported | RW
40139 | Ramp rate (PQGra) |  |  | supported | RW
40140 | PQMax_SF |  |  | 0 | R
40141 | PQLimPct_SF |  |  | -1 | R
40142 | PQGra_SF |  |  | 0 | R
40143 | Control priority (CtlPr) |  |  | supported | RW
|  |  | REAL | supported
|  |  | REACTIVE | supported
40144 | Enable arbitrage control (PQSet_Ena) |  |  | supported | RW
|  |  | DISABLE | supported
|  |  | ENABLE | supported
|  |  | UPDATE | supported
40145 | Connect (Conn) |  |  | supported | RW
|  |  | DISCONNECT | supported
|  |  | CONNECT | supported

## 120
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40146 | ID |  |  | 120
40147 | L |  |  | 26
40148 | DERTyp |  |  | supported | R
|  |  | PV | supported
|  |  | PV_STOR | supported
40149 | WRtg |  |  | supported | R
40150 | WRtg_SF |  |  | 0 | R
40151 | VARtg |  |  | supported | R
40152 | VARtg_SF |  |  | 0 | R
40153 | VArRtgQ1 |  |  | supported | R
40154 | VArRtgQ2 |  |  | supported | R
40155 | VArRtgQ3 |  |  | supported | R
40156 | VArRtgQ4 |  |  | supported | R
40157 | VArRtg_SF |  |  | 0 | R
40158 | ARtg |  |  | supported | R
40159 | ARtg_SF |  |  | -2 | R
40160 | PFRtgQ1 |  |  | supported | R
40161 | PFRtgQ2 |  |  | supported | R
40162 | PFRtgQ3 |  |  | supported | R
40163 | PFRtgQ4 |  |  | supported | R
40164 | PFRtg_SF |  |  | -3 | R
40165 | WHRtg |  |  | unimplemented | R
40166 | WHRtg_SF |  |  | 0 | R
40167 | AhrRtg |  |  | unimplemented | R
40168 | AhrRtg_SF |  |  | 0 | R
40169 | MaxChaRte |  |  | unimplemented | R
40170 | MaxChaRte_SF |  |  | 0 | R
40171 | MaxDisChaRte |  |  | unimplemented | R
40172 | MaxDisChaRte_SF |  |  | 0 | R
40173 | Pad |  |  |  | R

## 123
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40174 | ID |  |  | 123
40175 | L |  |  | 24
40176 | Conn_WinTms |  |  | unimplemented | RW
40177 | Conn_RvrtTms |  |  | unimplemented | RW
40178 | Conn |  |  | supported | RW
|  |  | DISCONNECT | supported
|  |  | CONNECT | supported
40179 | WMaxLimPct |  |  | supported | RW
40180 | WMaxLimPct_WinTms |  |  | unimplemented | RW
40181 | WMaxLimPct_RvrtTms |  |  | unimplemented | RW
40182 | WMaxLimPct_RmpTms |  |  | unimplemented | RW
40183 | WMaxLim_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40184 | OutPFSet |  |  | supported | RW
40185 | OutPFSet_WinTms |  |  | unimplemented | RW
40186 | OutPFSet_RvrtTms |  |  | unimplemented | RW
40187 | OutPFSet_RmpTms |  |  | unimplemented | RW
40188 | OutPFSet_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40189 | VArWMaxPct |  |  | unimplemented | RW
40190 | VArMaxPct |  |  | supported | RW
40191 | VArAvalPct |  |  | unimplemented | RW
40192 | VArPct_WinTms |  |  | unimplemented | RW
40193 | VArPct_RvrtTms |  |  | unimplemented | RW
40194 | VArPct_RmpTms |  |  | unimplemented | RW
40195 | VArPct_Mod |  |  | unimplemented | RW
|  |  | NONE | supported
|  |  | WMax | supported
|  |  | VArMax | supported
|  |  | VArAval | supported
40196 | VArPct_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40197 | WMaxLimPct_SF |  |  | -1 | R
40198 | OutPFSet_SF |  |  | -3 | R
40199 | VArPct_SF |  |  | -1 | R

## 126
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40200 | ID |  |  | 126
40201 | L |  |  | 226
40202 | ActCrv |  |  | supported | RW
40203 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40204 | WinTms |  |  | unimplemented | RW
40205 | RvrtTms |  |  | unimplemented | RW
40206 | RmpTms |  |  | unimplemented | RW
40207 | NCrv |  |  | supported | R
40208 | NPt |  |  | supported | R
40209 | V_SF |  |  | -1 | R
40210 | DeptRef_SF |  |  | -1 | R
40211 | RmpIncDec_SF |  |  | 0 | R
40212 | ActPt | 1 |  | supported | RW
40213 | DeptRef | 1 |  | supported | RW
|  |  | WMax | supported
|  |  | VArMax | supported
|  |  | VArAval | supported
40214 | V1 | 1 |  | supported | RW
40215 | VAr1 | 1 |  | supported | RW
40216 | V2 | 1 |  | supported | RW
40217 | VAr2 | 1 |  | supported | RW
40218 | V3 | 1 |  | supported | RW
40219 | VAr3 | 1 |  | supported | RW
40220 | V4 | 1 |  | supported | RW
40221 | VAr4 | 1 |  | supported | RW
40222 | V5 | 1 |  | supported | RW
40223 | VAr5 | 1 |  | supported | RW
40224 | V6 | 1 |  | supported | RW
40225 | VAr6 | 1 |  | supported | RW
40226 | V7 | 1 |  | supported | RW
40227 | VAr7 | 1 |  | supported | RW
40228 | V8 | 1 |  | supported | RW
40229 | VAr8 | 1 |  | supported | RW
40230 | V9 | 1 |  | supported | RW
40231 | VAr9 | 1 |  | supported | RW
40232 | V10 | 1 |  | supported | RW
40233 | VAr10 | 1 |  | supported | RW
40234 | V11 | 1 |  | unimplemented | RW
40235 | VAr11 | 1 |  | unimplemented | RW
40236 | V12 | 1 |  | unimplemented | RW
40237 | VAr12 | 1 |  | unimplemented | RW
40238 | V13 | 1 |  | unimplemented | RW
40239 | VAr13 | 1 |  | unimplemented | RW
40240 | V14 | 1 |  | unimplemented | RW
40241 | VAr14 | 1 |  | unimplemented | RW
40242 | V15 | 1 |  | unimplemented | RW
40243 | VAr15 | 1 |  | unimplemented | RW
40244 | V16 | 1 |  | unimplemented | RW
40245 | VAr16 | 1 |  | unimplemented | RW
40246 | V17 | 1 |  | unimplemented | RW
40247 | VAr17 | 1 |  | unimplemented | RW
40248 | V18 | 1 |  | unimplemented | RW
40249 | VAr18 | 1 |  | unimplemented | RW
40250 | V19 | 1 |  | unimplemented | RW
40251 | VAr19 | 1 |  | unimplemented | RW
40252 | V20 | 1 |  | unimplemented | RW
40253 | VAr20 | 1 |  | unimplemented | RW
40254 | CrvNam | 1 |  | unimplemented | RW
40262 | RmpTms | 1 |  | unimplemented | RW
40263 | RmpDecTmm | 1 |  | unimplemented | RW
40264 | RmpIncTmm | 1 |  | unimplemented | RW
40265 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
40266 | ActPt | 2 |  | supported | RW
40267 | DeptRef | 2 |  | supported | RW
40268 | V1 | 2 |  | supported | RW
40269 | VAr1 | 2 |  | supported | RW
40270 | V2 | 2 |  | supported | RW
40271 | VAr2 | 2 |  | supported | RW
40272 | V3 | 2 |  | supported | RW
40273 | VAr3 | 2 |  | supported | RW
40274 | V4 | 2 |  | supported | RW
40275 | VAr4 | 2 |  | supported | RW
40276 | V5 | 2 |  | supported | RW
40277 | VAr5 | 2 |  | supported | RW
40278 | V6 | 2 |  | supported | RW
40279 | VAr6 | 2 |  | supported | RW
40280 | V7 | 2 |  | supported | RW
40281 | VAr7 | 2 |  | supported | RW
40282 | V8 | 2 |  | supported | RW
40283 | VAr8 | 2 |  | supported | RW
40284 | V9 | 2 |  | supported | RW
40285 | VAr9 | 2 |  | supported | RW
40286 | V10 | 2 |  | supported | RW
40287 | VAr10 | 2 |  | supported | RW
40288 | V11 | 2 |  | unimplemented | RW
40289 | VAr11 | 2 |  | unimplemented | RW
40290 | V12 | 2 |  | unimplemented | RW
40291 | VAr12 | 2 |  | unimplemented | RW
40292 | V13 | 2 |  | unimplemented | RW
40293 | VAr13 | 2 |  | unimplemented | RW
40294 | V14 | 2 |  | unimplemented | RW
40295 | VAr14 | 2 |  | unimplemented | RW
40296 | V15 | 2 |  | unimplemented | RW
40297 | VAr15 | 2 |  | unimplemented | RW
40298 | V16 | 2 |  | unimplemented | RW
40299 | VAr16 | 2 |  | unimplemented | RW
40300 | V17 | 2 |  | unimplemented | RW
40301 | VAr17 | 2 |  | unimplemented | RW
40302 | V18 | 2 |  | unimplemented | RW
40303 | VAr18 | 2 |  | unimplemented | RW
40304 | V19 | 2 |  | unimplemented | RW
40305 | VAr19 | 2 |  | unimplemented | RW
40306 | V20 | 2 |  | unimplemented | RW
40307 | VAr20 | 2 |  | unimplemented | RW
40308 | CrvNam | 2 |  | unimplemented | RW
40316 | RmpTms | 2 |  | unimplemented | RW
40317 | RmpDecTmm | 2 |  | unimplemented | RW
40318 | RmpIncTmm | 2 |  | unimplemented | RW
40319 | ReadOnly | 2 |  | supported | R
40320 | ActPt | 3 |  | supported | RW
40321 | DeptRef | 3 |  | supported | RW
40322 | V1 | 3 |  | supported | RW
40323 | VAr1 | 3 |  | supported | RW
40324 | V2 | 3 |  | supported | RW
40325 | VAr2 | 3 |  | supported | RW
40326 | V3 | 3 |  | supported | RW
40327 | VAr3 | 3 |  | supported | RW
40328 | V4 | 3 |  | supported | RW
40329 | VAr4 | 3 |  | supported | RW
40330 | V5 | 3 |  | supported | RW
40331 | VAr5 | 3 |  | supported | RW
40332 | V6 | 3 |  | supported | RW
40333 | VAr6 | 3 |  | supported | RW
40334 | V7 | 3 |  | supported | RW
40335 | VAr7 | 3 |  | supported | RW
40336 | V8 | 3 |  | supported | RW
40337 | VAr8 | 3 |  | supported | RW
40338 | V9 | 3 |  | supported | RW
40339 | VAr9 | 3 |  | supported | RW
40340 | V10 | 3 |  | supported | RW
40341 | VAr10 | 3 |  | supported | RW
40342 | V11 | 3 |  | unimplemented | RW
40343 | VAr11 | 3 |  | unimplemented | RW
40344 | V12 | 3 |  | unimplemented | RW
40345 | VAr12 | 3 |  | unimplemented | RW
40346 | V13 | 3 |  | unimplemented | RW
40347 | VAr13 | 3 |  | unimplemented | RW
40348 | V14 | 3 |  | unimplemented | RW
40349 | VAr14 | 3 |  | unimplemented | RW
40350 | V15 | 3 |  | unimplemented | RW
40351 | VAr15 | 3 |  | unimplemented | RW
40352 | V16 | 3 |  | unimplemented | RW
40353 | VAr16 | 3 |  | unimplemented | RW
40354 | V17 | 3 |  | unimplemented | RW
40355 | VAr17 | 3 |  | unimplemented | RW
40356 | V18 | 3 |  | unimplemented | RW
40357 | VAr18 | 3 |  | unimplemented | RW
40358 | V19 | 3 |  | unimplemented | RW
40359 | VAr19 | 3 |  | unimplemented | RW
40360 | V20 | 3 |  | unimplemented | RW
40361 | VAr20 | 3 |  | unimplemented | RW
40362 | CrvNam | 3 |  | unimplemented | RW
40370 | RmpTms | 3 |  | unimplemented | RW
40371 | RmpDecTmm | 3 |  | unimplemented | RW
40372 | RmpIncTmm | 3 |  | unimplemented | RW
40373 | ReadOnly | 3 |  | supported | R
40374 | ActPt | 4 |  | supported | RW
40375 | DeptRef | 4 |  | supported | RW
40376 | V1 | 4 |  | supported | RW
40377 | VAr1 | 4 |  | supported | RW
40378 | V2 | 4 |  | supported | RW
40379 | VAr2 | 4 |  | supported | RW
40380 | V3 | 4 |  | supported | RW
40381 | VAr3 | 4 |  | supported | RW
40382 | V4 | 4 |  | supported | RW
40383 | VAr4 | 4 |  | supported | RW
40384 | V5 | 4 |  | supported | RW
40385 | VAr5 | 4 |  | supported | RW
40386 | V6 | 4 |  | supported | RW
40387 | VAr6 | 4 |  | supported | RW
40388 | V7 | 4 |  | supported | RW
40389 | VAr7 | 4 |  | supported | RW
40390 | V8 | 4 |  | supported | RW
40391 | VAr8 | 4 |  | supported | RW
40392 | V9 | 4 |  | supported | RW
40393 | VAr9 | 4 |  | supported | RW
40394 | V10 | 4 |  | supported | RW
40395 | VAr10 | 4 |  | supported | RW
40396 | V11 | 4 |  | unimplemented | RW
40397 | VAr11 | 4 |  | unimplemented | RW
40398 | V12 | 4 |  | unimplemented | RW
40399 | VAr12 | 4 |  | unimplemented | RW
40400 | V13 | 4 |  | unimplemented | RW
40401 | VAr13 | 4 |  | unimplemented | RW
40402 | V14 | 4 |  | unimplemented | RW
40403 | VAr14 | 4 |  | unimplemented | RW
40404 | V15 | 4 |  | unimplemented | RW
40405 | VAr15 | 4 |  | unimplemented | RW
40406 | V16 | 4 |  | unimplemented | RW
40407 | VAr16 | 4 |  | unimplemented | RW
40408 | V17 | 4 |  | unimplemented | RW
40409 | VAr17 | 4 |  | unimplemented | RW
40410 | V18 | 4 |  | unimplemented | RW
40411 | VAr18 | 4 |  | unimplemented | RW
40412 | V19 | 4 |  | unimplemented | RW
40413 | VAr19 | 4 |  | unimplemented | RW
40414 | V20 | 4 |  | unimplemented | RW
40415 | VAr20 | 4 |  | unimplemented | RW
40416 | CrvNam | 4 |  | unimplemented | RW
40424 | RmpTms | 4 |  | unimplemented | RW
40425 | RmpDecTmm | 4 |  | unimplemented | RW
40426 | RmpIncTmm | 4 |  | unimplemented | RW
40427 | ReadOnly | 4 |  | supported | R

## 129
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40428 | ID |  |  | 129
40429 | L |  |  | 210
40430 | ActCrv |  |  | supported | RW
40431 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40432 | WinTms |  |  | unimplemented | RW
40433 | RvrtTms |  |  | unimplemented | RW
40434 | RmpTms |  |  | unimplemented | RW
40435 | NCrv |  |  | supported | R
40436 | NPt |  |  | supported | R
40437 | Tms_SF |  |  | -2 | R
40438 | V_SF |  |  | -1 | R
40439 | Pad |  |  |  | R
40440 | ActPt | 1 |  | supported | RW
40441 | Tms1 | 1 |  | supported | RW
40442 | V1 | 1 |  | supported | RW
40443 | Tms2 | 1 |  | supported | RW
40444 | V2 | 1 |  | supported | RW
40445 | Tms3 | 1 |  | supported | RW
40446 | V3 | 1 |  | supported | RW
40447 | Tms4 | 1 |  | supported | RW
40448 | V4 | 1 |  | supported | RW
40449 | Tms5 | 1 |  | supported | RW
40450 | V5 | 1 |  | supported | RW
40451 | Tms6 | 1 |  | supported | RW
40452 | V6 | 1 |  | supported | RW
40453 | Tms7 | 1 |  | supported | RW
40454 | V7 | 1 |  | supported | RW
40455 | Tms8 | 1 |  | supported | RW
40456 | V8 | 1 |  | supported | RW
40457 | Tms9 | 1 |  | supported | RW
40458 | V9 | 1 |  | supported | RW
40459 | Tms10 | 1 |  | supported | RW
40460 | V10 | 1 |  | supported | RW
40461 | Tms11 | 1 |  | unimplemented | RW
40462 | V11 | 1 |  | unimplemented | RW
40463 | Tms12 | 1 |  | unimplemented | RW
40464 | V12 | 1 |  | unimplemented | RW
40465 | Tms13 | 1 |  | unimplemented | RW
40466 | V13 | 1 |  | unimplemented | RW
40467 | Tms14 | 1 |  | unimplemented | RW
40468 | V14 | 1 |  | unimplemented | RW
40469 | Tms15 | 1 |  | unimplemented | RW
40470 | V15 | 1 |  | unimplemented | RW
40471 | Tms16 | 1 |  | unimplemented | RW
40472 | V16 | 1 |  | unimplemented | RW
40473 | Tms17 | 1 |  | unimplemented | RW
40474 | V17 | 1 |  | unimplemented | RW
40475 | Tms18 | 1 |  | unimplemented | RW
40476 | V18 | 1 |  | unimplemented | RW
40477 | Tms19 | 1 |  | unimplemented | RW
40478 | V19 | 1 |  | unimplemented | RW
40479 | Tms20 | 1 |  | unimplemented | RW
40480 | V20 | 1 |  | unimplemented | RW
40481 | CrvNam | 1 |  | unimplemented | RW
40489 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
40490 | ActPt | 2 |  | supported | RW
40491 | Tms1 | 2 |  | supported | RW
40492 | V1 | 2 |  | supported | RW
40493 | Tms2 | 2 |  | supported | RW
40494 | V2 | 2 |  | supported | RW
40495 | Tms3 | 2 |  | supported | RW
40496 | V3 | 2 |  | supported | RW
40497 | Tms4 | 2 |  | supported | RW
40498 | V4 | 2 |  | supported | RW
40499 | Tms5 | 2 |  | supported | RW
40500 | V5 | 2 |  | supported | RW
40501 | Tms6 | 2 |  | supported | RW
40502 | V6 | 2 |  | supported | RW
40503 | Tms7 | 2 |  | supported | RW
40504 | V7 | 2 |  | supported | RW
40505 | Tms8 | 2 |  | supported | RW
40506 | V8 | 2 |  | supported | RW
40507 | Tms9 | 2 |  | supported | RW
40508 | V9 | 2 |  | supported | RW
40509 | Tms10 | 2 |  | supported | RW
40510 | V10 | 2 |  | supported | RW
40511 | Tms11 | 2 |  | unimplemented | RW
40512 | V11 | 2 |  | unimplemented | RW
40513 | Tms12 | 2 |  | unimplemented | RW
40514 | V12 | 2 |  | unimplemented | RW
40515 | Tms13 | 2 |  | unimplemented | RW
40516 | V13 | 2 |  | unimplemented | RW
40517 | Tms14 | 2 |  | unimplemented | RW
40518 | V14 | 2 |  | unimplemented | RW
40519 | Tms15 | 2 |  | unimplemented | RW
40520 | V15 | 2 |  | unimplemented | RW
40521 | Tms16 | 2 |  | unimplemented | RW
40522 | V16 | 2 |  | unimplemented | RW
40523 | Tms17 | 2 |  | unimplemented | RW
40524 | V17 | 2 |  | unimplemented | RW
40525 | Tms18 | 2 |  | unimplemented | RW
40526 | V18 | 2 |  | unimplemented | RW
40527 | Tms19 | 2 |  | unimplemented | RW
40528 | V19 | 2 |  | unimplemented | RW
40529 | Tms20 | 2 |  | unimplemented | RW
40530 | V20 | 2 |  | unimplemented | RW
40531 | CrvNam | 2 |  | unimplemented | RW
40539 | ReadOnly | 2 |  | supported | R
40540 | ActPt | 3 |  | supported | RW
40541 | Tms1 | 3 |  | supported | RW
40542 | V1 | 3 |  | supported | RW
40543 | Tms2 | 3 |  | supported | RW
40544 | V2 | 3 |  | supported | RW
40545 | Tms3 | 3 |  | supported | RW
40546 | V3 | 3 |  | supported | RW
40547 | Tms4 | 3 |  | supported | RW
40548 | V4 | 3 |  | supported | RW
40549 | Tms5 | 3 |  | supported | RW
40550 | V5 | 3 |  | supported | RW
40551 | Tms6 | 3 |  | supported | RW
40552 | V6 | 3 |  | supported | RW
40553 | Tms7 | 3 |  | supported | RW
40554 | V7 | 3 |  | supported | RW
40555 | Tms8 | 3 |  | supported | RW
40556 | V8 | 3 |  | supported | RW
40557 | Tms9 | 3 |  | supported | RW
40558 | V9 | 3 |  | supported | RW
40559 | Tms10 | 3 |  | supported | RW
40560 | V10 | 3 |  | supported | RW
40561 | Tms11 | 3 |  | unimplemented | RW
40562 | V11 | 3 |  | unimplemented | RW
40563 | Tms12 | 3 |  | unimplemented | RW
40564 | V12 | 3 |  | unimplemented | RW
40565 | Tms13 | 3 |  | unimplemented | RW
40566 | V13 | 3 |  | unimplemented | RW
40567 | Tms14 | 3 |  | unimplemented | RW
40568 | V14 | 3 |  | unimplemented | RW
40569 | Tms15 | 3 |  | unimplemented | RW
40570 | V15 | 3 |  | unimplemented | RW
40571 | Tms16 | 3 |  | unimplemented | RW
40572 | V16 | 3 |  | unimplemented | RW
40573 | Tms17 | 3 |  | unimplemented | RW
40574 | V17 | 3 |  | unimplemented | RW
40575 | Tms18 | 3 |  | unimplemented | RW
40576 | V18 | 3 |  | unimplemented | RW
40577 | Tms19 | 3 |  | unimplemented | RW
40578 | V19 | 3 |  | unimplemented | RW
40579 | Tms20 | 3 |  | unimplemented | RW
40580 | V20 | 3 |  | unimplemented | RW
40581 | CrvNam | 3 |  | unimplemented | RW
40589 | ReadOnly | 3 |  | supported | R
40590 | ActPt | 4 |  | supported | RW
40591 | Tms1 | 4 |  | supported | RW
40592 | V1 | 4 |  | supported | RW
40593 | Tms2 | 4 |  | supported | RW
40594 | V2 | 4 |  | supported | RW
40595 | Tms3 | 4 |  | supported | RW
40596 | V3 | 4 |  | supported | RW
40597 | Tms4 | 4 |  | supported | RW
40598 | V4 | 4 |  | supported | RW
40599 | Tms5 | 4 |  | supported | RW
40600 | V5 | 4 |  | supported | RW
40601 | Tms6 | 4 |  | supported | RW
40602 | V6 | 4 |  | supported | RW
40603 | Tms7 | 4 |  | supported | RW
40604 | V7 | 4 |  | supported | RW
40605 | Tms8 | 4 |  | supported | RW
40606 | V8 | 4 |  | supported | RW
40607 | Tms9 | 4 |  | supported | RW
40608 | V9 | 4 |  | supported | RW
40609 | Tms10 | 4 |  | supported | RW
40610 | V10 | 4 |  | supported | RW
40611 | Tms11 | 4 |  | unimplemented | RW
40612 | V11 | 4 |  | unimplemented | RW
40613 | Tms12 | 4 |  | unimplemented | RW
40614 | V12 | 4 |  | unimplemented | RW
40615 | Tms13 | 4 |  | unimplemented | RW
40616 | V13 | 4 |  | unimplemented | RW
40617 | Tms14 | 4 |  | unimplemented | RW
40618 | V14 | 4 |  | unimplemented | RW
40619 | Tms15 | 4 |  | unimplemented | RW
40620 | V15 | 4 |  | unimplemented | RW
40621 | Tms16 | 4 |  | unimplemented | RW
40622 | V16 | 4 |  | unimplemented | RW
40623 | Tms17 | 4 |  | unimplemented | RW
40624 | V17 | 4 |  | unimplemented | RW
40625 | Tms18 | 4 |  | unimplemented | RW
40626 | V18 | 4 |  | unimplemented | RW
40627 | Tms19 | 4 |  | unimplemented | RW
40628 | V19 | 4 |  | unimplemented | RW
40629 | Tms20 | 4 |  | unimplemented | RW
40630 | V20 | 4 |  | unimplemented | RW
40631 | CrvNam | 4 |  | unimplemented | RW
40639 | ReadOnly | 4 |  | supported | R

## 130
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40640 | ID |  |  | 130
40641 | L |  |  | 210
40642 | ActCrv |  |  | supported | RW
40643 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40644 | WinTms |  |  | unimplemented | RW
40645 | RvrtTms |  |  | unimplemented | RW
40646 | RmpTms |  |  | unimplemented | RW
40647 | NCrv |  |  | supported | R
40648 | NPt |  |  | supported | R
40649 | Tms_SF |  |  | -2 | R
40650 | V_SF |  |  | -1 | R
40651 | Pad |  |  |  | R
40652 | ActPt | 1 |  | supported | RW
40653 | Tms1 | 1 |  | supported | RW
40654 | V1 | 1 |  | supported | RW
40655 | Tms2 | 1 |  | supported | RW
40656 | V2 | 1 |  | supported | RW
40657 | Tms3 | 1 |  | supported | RW
40658 | V3 | 1 |  | supported | RW
40659 | Tms4 | 1 |  | supported | RW
40660 | V4 | 1 |  | supported | RW
40661 | Tms5 | 1 |  | supported | RW
40662 | V5 | 1 |  | supported | RW
40663 | Tms6 | 1 |  | supported | RW
40664 | V6 | 1 |  | supported | RW
40665 | Tms7 | 1 |  | supported | RW
40666 | V7 | 1 |  | supported | RW
40667 | Tms8 | 1 |  | supported | RW
40668 | V8 | 1 |  | supported | RW
40669 | Tms9 | 1 |  | supported | RW
40670 | V9 | 1 |  | supported | RW
40671 | Tms10 | 1 |  | supported | RW
40672 | V10 | 1 |  | supported | RW
40673 | Tms11 | 1 |  | unimplemented | RW
40674 | V11 | 1 |  | unimplemented | RW
40675 | Tms12 | 1 |  | unimplemented | RW
40676 | V12 | 1 |  | unimplemented | RW
40677 | Tms13 | 1 |  | unimplemented | RW
40678 | V13 | 1 |  | unimplemented | RW
40679 | Tms14 | 1 |  | unimplemented | RW
40680 | V14 | 1 |  | unimplemented | RW
40681 | Tms15 | 1 |  | unimplemented | RW
40682 | V15 | 1 |  | unimplemented | RW
40683 | Tms16 | 1 |  | unimplemented | RW
40684 | V16 | 1 |  | unimplemented | RW
40685 | Tms17 | 1 |  | unimplemented | RW
40686 | V17 | 1 |  | unimplemented | RW
40687 | Tms18 | 1 |  | unimplemented | RW
40688 | V18 | 1 |  | unimplemented | RW
40689 | Tms19 | 1 |  | unimplemented | RW
40690 | V19 | 1 |  | unimplemented | RW
40691 | Tms20 | 1 |  | unimplemented | RW
40692 | V20 | 1 |  | unimplemented | RW
40693 | CrvNam | 1 |  | unimplemented | RW
40701 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
40702 | ActPt | 2 |  | supported | RW
40703 | Tms1 | 2 |  | supported | RW
40704 | V1 | 2 |  | supported | RW
40705 | Tms2 | 2 |  | supported | RW
40706 | V2 | 2 |  | supported | RW
40707 | Tms3 | 2 |  | supported | RW
40708 | V3 | 2 |  | supported | RW
40709 | Tms4 | 2 |  | supported | RW
40710 | V4 | 2 |  | supported | RW
40711 | Tms5 | 2 |  | supported | RW
40712 | V5 | 2 |  | supported | RW
40713 | Tms6 | 2 |  | supported | RW
40714 | V6 | 2 |  | supported | RW
40715 | Tms7 | 2 |  | supported | RW
40716 | V7 | 2 |  | supported | RW
40717 | Tms8 | 2 |  | supported | RW
40718 | V8 | 2 |  | supported | RW
40719 | Tms9 | 2 |  | supported | RW
40720 | V9 | 2 |  | supported | RW
40721 | Tms10 | 2 |  | supported | RW
40722 | V10 | 2 |  | supported | RW
40723 | Tms11 | 2 |  | unimplemented | RW
40724 | V11 | 2 |  | unimplemented | RW
40725 | Tms12 | 2 |  | unimplemented | RW
40726 | V12 | 2 |  | unimplemented | RW
40727 | Tms13 | 2 |  | unimplemented | RW
40728 | V13 | 2 |  | unimplemented | RW
40729 | Tms14 | 2 |  | unimplemented | RW
40730 | V14 | 2 |  | unimplemented | RW
40731 | Tms15 | 2 |  | unimplemented | RW
40732 | V15 | 2 |  | unimplemented | RW
40733 | Tms16 | 2 |  | unimplemented | RW
40734 | V16 | 2 |  | unimplemented | RW
40735 | Tms17 | 2 |  | unimplemented | RW
40736 | V17 | 2 |  | unimplemented | RW
40737 | Tms18 | 2 |  | unimplemented | RW
40738 | V18 | 2 |  | unimplemented | RW
40739 | Tms19 | 2 |  | unimplemented | RW
40740 | V19 | 2 |  | unimplemented | RW
40741 | Tms20 | 2 |  | unimplemented | RW
40742 | V20 | 2 |  | unimplemented | RW
40743 | CrvNam | 2 |  | unimplemented | RW
40751 | ReadOnly | 2 |  | supported | R
40752 | ActPt | 3 |  | supported | RW
40753 | Tms1 | 3 |  | supported | RW
40754 | V1 | 3 |  | supported | RW
40755 | Tms2 | 3 |  | supported | RW
40756 | V2 | 3 |  | supported | RW
40757 | Tms3 | 3 |  | supported | RW
40758 | V3 | 3 |  | supported | RW
40759 | Tms4 | 3 |  | supported | RW
40760 | V4 | 3 |  | supported | RW
40761 | Tms5 | 3 |  | supported | RW
40762 | V5 | 3 |  | supported | RW
40763 | Tms6 | 3 |  | supported | RW
40764 | V6 | 3 |  | supported | RW
40765 | Tms7 | 3 |  | supported | RW
40766 | V7 | 3 |  | supported | RW
40767 | Tms8 | 3 |  | supported | RW
40768 | V8 | 3 |  | supported | RW
40769 | Tms9 | 3 |  | supported | RW
40770 | V9 | 3 |  | supported | RW
40771 | Tms10 | 3 |  | supported | RW
40772 | V10 | 3 |  | supported | RW
40773 | Tms11 | 3 |  | unimplemented | RW
40774 | V11 | 3 |  | unimplemented | RW
40775 | Tms12 | 3 |  | unimplemented | RW
40776 | V12 | 3 |  | unimplemented | RW
40777 | Tms13 | 3 |  | unimplemented | RW
40778 | V13 | 3 |  | unimplemented | RW
40779 | Tms14 | 3 |  | unimplemented | RW
40780 | V14 | 3 |  | unimplemented | RW
40781 | Tms15 | 3 |  | unimplemented | RW
40782 | V15 | 3 |  | unimplemented | RW
40783 | Tms16 | 3 |  | unimplemented | RW
40784 | V16 | 3 |  | unimplemented | RW
40785 | Tms17 | 3 |  | unimplemented | RW
40786 | V17 | 3 |  | unimplemented | RW
40787 | Tms18 | 3 |  | unimplemented | RW
40788 | V18 | 3 |  | unimplemented | RW
40789 | Tms19 | 3 |  | unimplemented | RW
40790 | V19 | 3 |  | unimplemented | RW
40791 | Tms20 | 3 |  | unimplemented | RW
40792 | V20 | 3 |  | unimplemented | RW
40793 | CrvNam | 3 |  | unimplemented | RW
40801 | ReadOnly | 3 |  | supported | R
40802 | ActPt | 4 |  | supported | RW
40803 | Tms1 | 4 |  | supported | RW
40804 | V1 | 4 |  | supported | RW
40805 | Tms2 | 4 |  | supported | RW
40806 | V2 | 4 |  | supported | RW
40807 | Tms3 | 4 |  | supported | RW
40808 | V3 | 4 |  | supported | RW
40809 | Tms4 | 4 |  | supported | RW
40810 | V4 | 4 |  | supported | RW
40811 | Tms5 | 4 |  | supported | RW
40812 | V5 | 4 |  | supported | RW
40813 | Tms6 | 4 |  | supported | RW
40814 | V6 | 4 |  | supported | RW
40815 | Tms7 | 4 |  | supported | RW
40816 | V7 | 4 |  | supported | RW
40817 | Tms8 | 4 |  | supported | RW
40818 | V8 | 4 |  | supported | RW
40819 | Tms9 | 4 |  | supported | RW
40820 | V9 | 4 |  | supported | RW
40821 | Tms10 | 4 |  | supported | RW
40822 | V10 | 4 |  | supported | RW
40823 | Tms11 | 4 |  | unimplemented | RW
40824 | V11 | 4 |  | unimplemented | RW
40825 | Tms12 | 4 |  | unimplemented | RW
40826 | V12 | 4 |  | unimplemented | RW
40827 | Tms13 | 4 |  | unimplemented | RW
40828 | V13 | 4 |  | unimplemented | RW
40829 | Tms14 | 4 |  | unimplemented | RW
40830 | V14 | 4 |  | unimplemented | RW
40831 | Tms15 | 4 |  | unimplemented | RW
40832 | V15 | 4 |  | unimplemented | RW
40833 | Tms16 | 4 |  | unimplemented | RW
40834 | V16 | 4 |  | unimplemented | RW
40835 | Tms17 | 4 |  | unimplemented | RW
40836 | V17 | 4 |  | unimplemented | RW
40837 | Tms18 | 4 |  | unimplemented | RW
40838 | V18 | 4 |  | unimplemented | RW
40839 | Tms19 | 4 |  | unimplemented | RW
40840 | V19 | 4 |  | unimplemented | RW
40841 | Tms20 | 4 |  | unimplemented | RW
40842 | V20 | 4 |  | unimplemented | RW
40843 | CrvNam | 4 |  | unimplemented | RW
40851 | ReadOnly | 4 |  | supported | R

## 64229
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40852 | ID |  |  | 64229
40853 | L |  |  | 370
40854 | ActCrv |  |  | supported | RW
40855 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40856 | WinTms |  |  | unimplemented | RW
40857 | RvrtTms |  |  | unimplemented | RW
40858 | RmpTms |  |  | unimplemented | RW
40859 | NCrv |  |  | supported | R
40860 | NPt |  |  | supported | R
40861 | Tms_SF |  |  | -6 | R
40862 | V_SF |  |  | -1 | R
40863 | Pad |  |  |  | R
40864 | ActPt | 1 |  | supported | RW
40865 | Tms1 | 1 |  | supported | RW
40867 | V1 | 1 |  | supported | RW
40868 | Fn1 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40869 | Tms2 | 1 |  | supported | RW
40871 | V2 | 1 |  | supported | RW
40872 | Fn2 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40873 | Tms3 | 1 |  | supported | RW
40875 | V3 | 1 |  | supported | RW
40876 | Fn3 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40877 | Tms4 | 1 |  | supported | RW
40879 | V4 | 1 |  | supported | RW
40880 | Fn4 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40881 | Tms5 | 1 |  | supported | RW
40883 | V5 | 1 |  | supported | RW
40884 | Fn5 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40885 | Tms6 | 1 |  | supported | RW
40887 | V6 | 1 |  | supported | RW
40888 | Fn6 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40889 | Tms7 | 1 |  | supported | RW
40891 | V7 | 1 |  | supported | RW
40892 | Fn7 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40893 | Tms8 | 1 |  | supported | RW
40895 | V8 | 1 |  | supported | RW
40896 | Fn8 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40897 | Tms9 | 1 |  | supported | RW
40899 | V9 | 1 |  | supported | RW
40900 | Fn9 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40901 | Tms10 | 1 |  | supported | RW
40903 | V10 | 1 |  | supported | RW
40904 | Fn10 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40905 | Tms11 | 1 |  | unimplemented | RW
40907 | V11 | 1 |  | unimplemented | RW
40908 | Fn11 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
40909 | Tms12 | 1 |  | unimplemented | RW
40911 | V12 | 1 |  | unimplemented | RW
40912 | Fn12 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
40913 | Tms13 | 1 |  | unimplemented | RW
40915 | V13 | 1 |  | unimplemented | RW
40916 | Fn13 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
40917 | Tms14 | 1 |  | unimplemented | RW
40919 | V14 | 1 |  | unimplemented | RW
40920 | Fn14 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
40921 | Tms15 | 1 |  | unimplemented | RW
40923 | V15 | 1 |  | unimplemented | RW
40924 | Fn15 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
40925 | Tms16 | 1 |  | unimplemented | RW
40927 | V16 | 1 |  | unimplemented | RW
40928 | Fn16 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
40929 | Tms17 | 1 |  | unimplemented | RW
40931 | V17 | 1 |  | unimplemented | RW
40932 | Fn17 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
40933 | Tms18 | 1 |  | unimplemented | RW
40935 | V18 | 1 |  | unimplemented | RW
40936 | Fn18 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
40937 | Tms19 | 1 |  | unimplemented | RW
40939 | V19 | 1 |  | unimplemented | RW
40940 | Fn19 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
40941 | Tms20 | 1 |  | unimplemented | RW
40943 | V20 | 1 |  | unimplemented | RW
40944 | Fn20 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
40945 | CrvNam | 1 |  | unimplemented | RW
40953 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
40954 | ActPt | 2 |  | supported | RW
40955 | Tms1 | 2 |  | supported | RW
40957 | V1 | 2 |  | supported | RW
40958 | Fn1 | 2 |  | supported | RW
40959 | Tms2 | 2 |  | supported | RW
40961 | V2 | 2 |  | supported | RW
40962 | Fn2 | 2 |  | supported | RW
40963 | Tms3 | 2 |  | supported | RW
40965 | V3 | 2 |  | supported | RW
40966 | Fn3 | 2 |  | supported | RW
40967 | Tms4 | 2 |  | supported | RW
40969 | V4 | 2 |  | supported | RW
40970 | Fn4 | 2 |  | supported | RW
40971 | Tms5 | 2 |  | supported | RW
40973 | V5 | 2 |  | supported | RW
40974 | Fn5 | 2 |  | supported | RW
40975 | Tms6 | 2 |  | supported | RW
40977 | V6 | 2 |  | supported | RW
40978 | Fn6 | 2 |  | supported | RW
40979 | Tms7 | 2 |  | supported | RW
40981 | V7 | 2 |  | supported | RW
40982 | Fn7 | 2 |  | supported | RW
40983 | Tms8 | 2 |  | supported | RW
40985 | V8 | 2 |  | supported | RW
40986 | Fn8 | 2 |  | supported | RW
40987 | Tms9 | 2 |  | supported | RW
40989 | V9 | 2 |  | supported | RW
40990 | Fn9 | 2 |  | supported | RW
40991 | Tms10 | 2 |  | supported | RW
40993 | V10 | 2 |  | supported | RW
40994 | Fn10 | 2 |  | supported | RW
40995 | Tms11 | 2 |  | unimplemented | RW
40997 | V11 | 2 |  | unimplemented | RW
40998 | Fn11 | 2 |  | unimplemented | RW
40999 | Tms12 | 2 |  | unimplemented | RW
41001 | V12 | 2 |  | unimplemented | RW
41002 | Fn12 | 2 |  | unimplemented | RW
41003 | Tms13 | 2 |  | unimplemented | RW
41005 | V13 | 2 |  | unimplemented | RW
41006 | Fn13 | 2 |  | unimplemented | RW
41007 | Tms14 | 2 |  | unimplemented | RW
41009 | V14 | 2 |  | unimplemented | RW
41010 | Fn14 | 2 |  | unimplemented | RW
41011 | Tms15 | 2 |  | unimplemented | RW
41013 | V15 | 2 |  | unimplemented | RW
41014 | Fn15 | 2 |  | unimplemented | RW
41015 | Tms16 | 2 |  | unimplemented | RW
41017 | V16 | 2 |  | unimplemented | RW
41018 | Fn16 | 2 |  | unimplemented | RW
41019 | Tms17 | 2 |  | unimplemented | RW
41021 | V17 | 2 |  | unimplemented | RW
41022 | Fn17 | 2 |  | unimplemented | RW
41023 | Tms18 | 2 |  | unimplemented | RW
41025 | V18 | 2 |  | unimplemented | RW
41026 | Fn18 | 2 |  | unimplemented | RW
41027 | Tms19 | 2 |  | unimplemented | RW
41029 | V19 | 2 |  | unimplemented | RW
41030 | Fn19 | 2 |  | unimplemented | RW
41031 | Tms20 | 2 |  | unimplemented | RW
41033 | V20 | 2 |  | unimplemented | RW
41034 | Fn20 | 2 |  | unimplemented | RW
41035 | CrvNam | 2 |  | unimplemented | RW
41043 | ReadOnly | 2 |  | supported | R
41044 | ActPt | 3 |  | supported | RW
41045 | Tms1 | 3 |  | supported | RW
41047 | V1 | 3 |  | supported | RW
41048 | Fn1 | 3 |  | supported | RW
41049 | Tms2 | 3 |  | supported | RW
41051 | V2 | 3 |  | supported | RW
41052 | Fn2 | 3 |  | supported | RW
41053 | Tms3 | 3 |  | supported | RW
41055 | V3 | 3 |  | supported | RW
41056 | Fn3 | 3 |  | supported | RW
41057 | Tms4 | 3 |  | supported | RW
41059 | V4 | 3 |  | supported | RW
41060 | Fn4 | 3 |  | supported | RW
41061 | Tms5 | 3 |  | supported | RW
41063 | V5 | 3 |  | supported | RW
41064 | Fn5 | 3 |  | supported | RW
41065 | Tms6 | 3 |  | supported | RW
41067 | V6 | 3 |  | supported | RW
41068 | Fn6 | 3 |  | supported | RW
41069 | Tms7 | 3 |  | supported | RW
41071 | V7 | 3 |  | supported | RW
41072 | Fn7 | 3 |  | supported | RW
41073 | Tms8 | 3 |  | supported | RW
41075 | V8 | 3 |  | supported | RW
41076 | Fn8 | 3 |  | supported | RW
41077 | Tms9 | 3 |  | supported | RW
41079 | V9 | 3 |  | supported | RW
41080 | Fn9 | 3 |  | supported | RW
41081 | Tms10 | 3 |  | supported | RW
41083 | V10 | 3 |  | supported | RW
41084 | Fn10 | 3 |  | supported | RW
41085 | Tms11 | 3 |  | unimplemented | RW
41087 | V11 | 3 |  | unimplemented | RW
41088 | Fn11 | 3 |  | unimplemented | RW
41089 | Tms12 | 3 |  | unimplemented | RW
41091 | V12 | 3 |  | unimplemented | RW
41092 | Fn12 | 3 |  | unimplemented | RW
41093 | Tms13 | 3 |  | unimplemented | RW
41095 | V13 | 3 |  | unimplemented | RW
41096 | Fn13 | 3 |  | unimplemented | RW
41097 | Tms14 | 3 |  | unimplemented | RW
41099 | V14 | 3 |  | unimplemented | RW
41100 | Fn14 | 3 |  | unimplemented | RW
41101 | Tms15 | 3 |  | unimplemented | RW
41103 | V15 | 3 |  | unimplemented | RW
41104 | Fn15 | 3 |  | unimplemented | RW
41105 | Tms16 | 3 |  | unimplemented | RW
41107 | V16 | 3 |  | unimplemented | RW
41108 | Fn16 | 3 |  | unimplemented | RW
41109 | Tms17 | 3 |  | unimplemented | RW
41111 | V17 | 3 |  | unimplemented | RW
41112 | Fn17 | 3 |  | unimplemented | RW
41113 | Tms18 | 3 |  | unimplemented | RW
41115 | V18 | 3 |  | unimplemented | RW
41116 | Fn18 | 3 |  | unimplemented | RW
41117 | Tms19 | 3 |  | unimplemented | RW
41119 | V19 | 3 |  | unimplemented | RW
41120 | Fn19 | 3 |  | unimplemented | RW
41121 | Tms20 | 3 |  | unimplemented | RW
41123 | V20 | 3 |  | unimplemented | RW
41124 | Fn20 | 3 |  | unimplemented | RW
41125 | CrvNam | 3 |  | unimplemented | RW
41133 | ReadOnly | 3 |  | supported | R
41134 | ActPt | 4 |  | supported | RW
41135 | Tms1 | 4 |  | supported | RW
41137 | V1 | 4 |  | supported | RW
41138 | Fn1 | 4 |  | supported | RW
41139 | Tms2 | 4 |  | supported | RW
41141 | V2 | 4 |  | supported | RW
41142 | Fn2 | 4 |  | supported | RW
41143 | Tms3 | 4 |  | supported | RW
41145 | V3 | 4 |  | supported | RW
41146 | Fn3 | 4 |  | supported | RW
41147 | Tms4 | 4 |  | supported | RW
41149 | V4 | 4 |  | supported | RW
41150 | Fn4 | 4 |  | supported | RW
41151 | Tms5 | 4 |  | supported | RW
41153 | V5 | 4 |  | supported | RW
41154 | Fn5 | 4 |  | supported | RW
41155 | Tms6 | 4 |  | supported | RW
41157 | V6 | 4 |  | supported | RW
41158 | Fn6 | 4 |  | supported | RW
41159 | Tms7 | 4 |  | supported | RW
41161 | V7 | 4 |  | supported | RW
41162 | Fn7 | 4 |  | supported | RW
41163 | Tms8 | 4 |  | supported | RW
41165 | V8 | 4 |  | supported | RW
41166 | Fn8 | 4 |  | supported | RW
41167 | Tms9 | 4 |  | supported | RW
41169 | V9 | 4 |  | supported | RW
41170 | Fn9 | 4 |  | supported | RW
41171 | Tms10 | 4 |  | supported | RW
41173 | V10 | 4 |  | supported | RW
41174 | Fn10 | 4 |  | supported | RW
41175 | Tms11 | 4 |  | unimplemented | RW
41177 | V11 | 4 |  | unimplemented | RW
41178 | Fn11 | 4 |  | unimplemented | RW
41179 | Tms12 | 4 |  | unimplemented | RW
41181 | V12 | 4 |  | unimplemented | RW
41182 | Fn12 | 4 |  | unimplemented | RW
41183 | Tms13 | 4 |  | unimplemented | RW
41185 | V13 | 4 |  | unimplemented | RW
41186 | Fn13 | 4 |  | unimplemented | RW
41187 | Tms14 | 4 |  | unimplemented | RW
41189 | V14 | 4 |  | unimplemented | RW
41190 | Fn14 | 4 |  | unimplemented | RW
41191 | Tms15 | 4 |  | unimplemented | RW
41193 | V15 | 4 |  | unimplemented | RW
41194 | Fn15 | 4 |  | unimplemented | RW
41195 | Tms16 | 4 |  | unimplemented | RW
41197 | V16 | 4 |  | unimplemented | RW
41198 | Fn16 | 4 |  | unimplemented | RW
41199 | Tms17 | 4 |  | unimplemented | RW
41201 | V17 | 4 |  | unimplemented | RW
41202 | Fn17 | 4 |  | unimplemented | RW
41203 | Tms18 | 4 |  | unimplemented | RW
41205 | V18 | 4 |  | unimplemented | RW
41206 | Fn18 | 4 |  | unimplemented | RW
41207 | Tms19 | 4 |  | unimplemented | RW
41209 | V19 | 4 |  | unimplemented | RW
41210 | Fn19 | 4 |  | unimplemented | RW
41211 | Tms20 | 4 |  | unimplemented | RW
41213 | V20 | 4 |  | unimplemented | RW
41214 | Fn20 | 4 |  | unimplemented | RW
41215 | CrvNam | 4 |  | unimplemented | RW
41223 | ReadOnly | 4 |  | supported | R

## 64230
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
41224 | ID |  |  | 64230
41225 | L |  |  | 370
41226 | ActCrv |  |  | supported | RW
41227 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
41228 | WinTms |  |  | unimplemented | RW
41229 | RvrtTms |  |  | unimplemented | RW
41230 | RmpTms |  |  | unimplemented | RW
41231 | NCrv |  |  | supported | R
41232 | NPt |  |  | supported | R
41233 | Tms_SF |  |  | -6 | R
41234 | V_SF |  |  | -1 | R
41235 | Pad |  |  |  | R
41236 | ActPt | 1 |  | supported | RW
41237 | Tms1 | 1 |  | supported | RW
41239 | V1 | 1 |  | supported | RW
41240 | Fn1 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41241 | Tms2 | 1 |  | supported | RW
41243 | V2 | 1 |  | supported | RW
41244 | Fn2 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41245 | Tms3 | 1 |  | supported | RW
41247 | V3 | 1 |  | supported | RW
41248 | Fn3 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41249 | Tms4 | 1 |  | supported | RW
41251 | V4 | 1 |  | supported | RW
41252 | Fn4 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41253 | Tms5 | 1 |  | supported | RW
41255 | V5 | 1 |  | supported | RW
41256 | Fn5 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41257 | Tms6 | 1 |  | supported | RW
41259 | V6 | 1 |  | supported | RW
41260 | Fn6 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41261 | Tms7 | 1 |  | supported | RW
41263 | V7 | 1 |  | supported | RW
41264 | Fn7 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41265 | Tms8 | 1 |  | supported | RW
41267 | V8 | 1 |  | supported | RW
41268 | Fn8 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41269 | Tms9 | 1 |  | supported | RW
41271 | V9 | 1 |  | supported | RW
41272 | Fn9 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41273 | Tms10 | 1 |  | supported | RW
41275 | V10 | 1 |  | supported | RW
41276 | Fn10 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41277 | Tms11 | 1 |  | unimplemented | RW
41279 | V11 | 1 |  | unimplemented | RW
41280 | Fn11 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41281 | Tms12 | 1 |  | unimplemented | RW
41283 | V12 | 1 |  | unimplemented | RW
41284 | Fn12 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41285 | Tms13 | 1 |  | unimplemented | RW
41287 | V13 | 1 |  | unimplemented | RW
41288 | Fn13 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41289 | Tms14 | 1 |  | unimplemented | RW
41291 | V14 | 1 |  | unimplemented | RW
41292 | Fn14 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41293 | Tms15 | 1 |  | unimplemented | RW
41295 | V15 | 1 |  | unimplemented | RW
41296 | Fn15 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41297 | Tms16 | 1 |  | unimplemented | RW
41299 | V16 | 1 |  | unimplemented | RW
41300 | Fn16 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41301 | Tms17 | 1 |  | unimplemented | RW
41303 | V17 | 1 |  | unimplemented | RW
41304 | Fn17 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41305 | Tms18 | 1 |  | unimplemented | RW
41307 | V18 | 1 |  | unimplemented | RW
41308 | Fn18 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41309 | Tms19 | 1 |  | unimplemented | RW
41311 | V19 | 1 |  | unimplemented | RW
41312 | Fn19 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41313 | Tms20 | 1 |  | unimplemented | RW
41315 | V20 | 1 |  | unimplemented | RW
41316 | Fn20 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41317 | CrvNam | 1 |  | unimplemented | RW
41325 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
41326 | ActPt | 2 |  | supported | RW
41327 | Tms1 | 2 |  | supported | RW
41329 | V1 | 2 |  | supported | RW
41330 | Fn1 | 2 |  | supported | RW
41331 | Tms2 | 2 |  | supported | RW
41333 | V2 | 2 |  | supported | RW
41334 | Fn2 | 2 |  | supported | RW
41335 | Tms3 | 2 |  | supported | RW
41337 | V3 | 2 |  | supported | RW
41338 | Fn3 | 2 |  | supported | RW
41339 | Tms4 | 2 |  | supported | RW
41341 | V4 | 2 |  | supported | RW
41342 | Fn4 | 2 |  | supported | RW
41343 | Tms5 | 2 |  | supported | RW
41345 | V5 | 2 |  | supported | RW
41346 | Fn5 | 2 |  | supported | RW
41347 | Tms6 | 2 |  | supported | RW
41349 | V6 | 2 |  | supported | RW
41350 | Fn6 | 2 |  | supported | RW
41351 | Tms7 | 2 |  | supported | RW
41353 | V7 | 2 |  | supported | RW
41354 | Fn7 | 2 |  | supported | RW
41355 | Tms8 | 2 |  | supported | RW
41357 | V8 | 2 |  | supported | RW
41358 | Fn8 | 2 |  | supported | RW
41359 | Tms9 | 2 |  | supported | RW
41361 | V9 | 2 |  | supported | RW
41362 | Fn9 | 2 |  | supported | RW
41363 | Tms10 | 2 |  | supported | RW
41365 | V10 | 2 |  | supported | RW
41366 | Fn10 | 2 |  | supported | RW
41367 | Tms11 | 2 |  | unimplemented | RW
41369 | V11 | 2 |  | unimplemented | RW
41370 | Fn11 | 2 |  | unimplemented | RW
41371 | Tms12 | 2 |  | unimplemented | RW
41373 | V12 | 2 |  | unimplemented | RW
41374 | Fn12 | 2 |  | unimplemented | RW
41375 | Tms13 | 2 |  | unimplemented | RW
41377 | V13 | 2 |  | unimplemented | RW
41378 | Fn13 | 2 |  | unimplemented | RW
41379 | Tms14 | 2 |  | unimplemented | RW
41381 | V14 | 2 |  | unimplemented | RW
41382 | Fn14 | 2 |  | unimplemented | RW
41383 | Tms15 | 2 |  | unimplemented | RW
41385 | V15 | 2 |  | unimplemented | RW
41386 | Fn15 | 2 |  | unimplemented | RW
41387 | Tms16 | 2 |  | unimplemented | RW
41389 | V16 | 2 |  | unimplemented | RW
41390 | Fn16 | 2 |  | unimplemented | RW
41391 | Tms17 | 2 |  | unimplemented | RW
41393 | V17 | 2 |  | unimplemented | RW
41394 | Fn17 | 2 |  | unimplemented | RW
41395 | Tms18 | 2 |  | unimplemented | RW
41397 | V18 | 2 |  | unimplemented | RW
41398 | Fn18 | 2 |  | unimplemented | RW
41399 | Tms19 | 2 |  | unimplemented | RW
41401 | V19 | 2 |  | unimplemented | RW
41402 | Fn19 | 2 |  | unimplemented | RW
41403 | Tms20 | 2 |  | unimplemented | RW
41405 | V20 | 2 |  | unimplemented | RW
41406 | Fn20 | 2 |  | unimplemented | RW
41407 | CrvNam | 2 |  | unimplemented | RW
41415 | ReadOnly | 2 |  | supported | R
41416 | ActPt | 3 |  | supported | RW
41417 | Tms1 | 3 |  | supported | RW
41419 | V1 | 3 |  | supported | RW
41420 | Fn1 | 3 |  | supported | RW
41421 | Tms2 | 3 |  | supported | RW
41423 | V2 | 3 |  | supported | RW
41424 | Fn2 | 3 |  | supported | RW
41425 | Tms3 | 3 |  | supported | RW
41427 | V3 | 3 |  | supported | RW
41428 | Fn3 | 3 |  | supported | RW
41429 | Tms4 | 3 |  | supported | RW
41431 | V4 | 3 |  | supported | RW
41432 | Fn4 | 3 |  | supported | RW
41433 | Tms5 | 3 |  | supported | RW
41435 | V5 | 3 |  | supported | RW
41436 | Fn5 | 3 |  | supported | RW
41437 | Tms6 | 3 |  | supported | RW
41439 | V6 | 3 |  | supported | RW
41440 | Fn6 | 3 |  | supported | RW
41441 | Tms7 | 3 |  | supported | RW
41443 | V7 | 3 |  | supported | RW
41444 | Fn7 | 3 |  | supported | RW
41445 | Tms8 | 3 |  | supported | RW
41447 | V8 | 3 |  | supported | RW
41448 | Fn8 | 3 |  | supported | RW
41449 | Tms9 | 3 |  | supported | RW
41451 | V9 | 3 |  | supported | RW
41452 | Fn9 | 3 |  | supported | RW
41453 | Tms10 | 3 |  | supported | RW
41455 | V10 | 3 |  | supported | RW
41456 | Fn10 | 3 |  | supported | RW
41457 | Tms11 | 3 |  | unimplemented | RW
41459 | V11 | 3 |  | unimplemented | RW
41460 | Fn11 | 3 |  | unimplemented | RW
41461 | Tms12 | 3 |  | unimplemented | RW
41463 | V12 | 3 |  | unimplemented | RW
41464 | Fn12 | 3 |  | unimplemented | RW
41465 | Tms13 | 3 |  | unimplemented | RW
41467 | V13 | 3 |  | unimplemented | RW
41468 | Fn13 | 3 |  | unimplemented | RW
41469 | Tms14 | 3 |  | unimplemented | RW
41471 | V14 | 3 |  | unimplemented | RW
41472 | Fn14 | 3 |  | unimplemented | RW
41473 | Tms15 | 3 |  | unimplemented | RW
41475 | V15 | 3 |  | unimplemented | RW
41476 | Fn15 | 3 |  | unimplemented | RW
41477 | Tms16 | 3 |  | unimplemented | RW
41479 | V16 | 3 |  | unimplemented | RW
41480 | Fn16 | 3 |  | unimplemented | RW
41481 | Tms17 | 3 |  | unimplemented | RW
41483 | V17 | 3 |  | unimplemented | RW
41484 | Fn17 | 3 |  | unimplemented | RW
41485 | Tms18 | 3 |  | unimplemented | RW
41487 | V18 | 3 |  | unimplemented | RW
41488 | Fn18 | 3 |  | unimplemented | RW
41489 | Tms19 | 3 |  | unimplemented | RW
41491 | V19 | 3 |  | unimplemented | RW
41492 | Fn19 | 3 |  | unimplemented | RW
41493 | Tms20 | 3 |  | unimplemented | RW
41495 | V20 | 3 |  | unimplemented | RW
41496 | Fn20 | 3 |  | unimplemented | RW
41497 | CrvNam | 3 |  | unimplemented | RW
41505 | ReadOnly | 3 |  | supported | R
41506 | ActPt | 4 |  | supported | RW
41507 | Tms1 | 4 |  | supported | RW
41509 | V1 | 4 |  | supported | RW
41510 | Fn1 | 4 |  | supported | RW
41511 | Tms2 | 4 |  | supported | RW
41513 | V2 | 4 |  | supported | RW
41514 | Fn2 | 4 |  | supported | RW
41515 | Tms3 | 4 |  | supported | RW
41517 | V3 | 4 |  | supported | RW
41518 | Fn3 | 4 |  | supported | RW
41519 | Tms4 | 4 |  | supported | RW
41521 | V4 | 4 |  | supported | RW
41522 | Fn4 | 4 |  | supported | RW
41523 | Tms5 | 4 |  | supported | RW
41525 | V5 | 4 |  | supported | RW
41526 | Fn5 | 4 |  | supported | RW
41527 | Tms6 | 4 |  | supported | RW
41529 | V6 | 4 |  | supported | RW
41530 | Fn6 | 4 |  | supported | RW
41531 | Tms7 | 4 |  | supported | RW
41533 | V7 | 4 |  | supported | RW
41534 | Fn7 | 4 |  | supported | RW
41535 | Tms8 | 4 |  | supported | RW
41537 | V8 | 4 |  | supported | RW
41538 | Fn8 | 4 |  | supported | RW
41539 | Tms9 | 4 |  | supported | RW
41541 | V9 | 4 |  | supported | RW
41542 | Fn9 | 4 |  | supported | RW
41543 | Tms10 | 4 |  | supported | RW
41545 | V10 | 4 |  | supported | RW
41546 | Fn10 | 4 |  | supported | RW
41547 | Tms11 | 4 |  | unimplemented | RW
41549 | V11 | 4 |  | unimplemented | RW
41550 | Fn11 | 4 |  | unimplemented | RW
41551 | Tms12 | 4 |  | unimplemented | RW
41553 | V12 | 4 |  | unimplemented | RW
41554 | Fn12 | 4 |  | unimplemented | RW
41555 | Tms13 | 4 |  | unimplemented | RW
41557 | V13 | 4 |  | unimplemented | RW
41558 | Fn13 | 4 |  | unimplemented | RW
41559 | Tms14 | 4 |  | unimplemented | RW
41561 | V14 | 4 |  | unimplemented | RW
41562 | Fn14 | 4 |  | unimplemented | RW
41563 | Tms15 | 4 |  | unimplemented | RW
41565 | V15 | 4 |  | unimplemented | RW
41566 | Fn15 | 4 |  | unimplemented | RW
41567 | Tms16 | 4 |  | unimplemented | RW
41569 | V16 | 4 |  | unimplemented | RW
41570 | Fn16 | 4 |  | unimplemented | RW
41571 | Tms17 | 4 |  | unimplemented | RW
41573 | V17 | 4 |  | unimplemented | RW
41574 | Fn17 | 4 |  | unimplemented | RW
41575 | Tms18 | 4 |  | unimplemented | RW
41577 | V18 | 4 |  | unimplemented | RW
41578 | Fn18 | 4 |  | unimplemented | RW
41579 | Tms19 | 4 |  | unimplemented | RW
41581 | V19 | 4 |  | unimplemented | RW
41582 | Fn19 | 4 |  | unimplemented | RW
41583 | Tms20 | 4 |  | unimplemented | RW
41585 | V20 | 4 |  | unimplemented | RW
41586 | Fn20 | 4 |  | unimplemented | RW
41587 | CrvNam | 4 |  | unimplemented | RW
41595 | ReadOnly | 4 |  | supported | R

## 132
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
41596 | ID |  |  | 132
41597 | L |  |  | 226
41598 | ActCrv |  |  | supported | RW
41599 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
41600 | WinTms |  |  | unimplemented | RW
41601 | RvrtTms |  |  | unimplemented | RW
41602 | RmpTms |  |  | unimplemented | RW
41603 | NCrv |  |  | supported | R
41604 | NPt |  |  | supported | R
41605 | V_SF |  |  | -1 | R
41606 | DeptRef_SF |  |  | -1 | R
41607 | RmpIncDec_SF |  |  | 0 | R
41608 | ActPt | 1 |  | supported | RW
41609 | DeptRef | 1 |  | supported | RW
|  |  | %WMax | supported
|  |  | %WAval | supported
41610 | V1 | 1 |  | supported | RW
41611 | W1 | 1 |  | supported | RW
41612 | V2 | 1 |  | supported | RW
41613 | W2 | 1 |  | supported | RW
41614 | V3 | 1 |  | supported | RW
41615 | W3 | 1 |  | supported | RW
41616 | V4 | 1 |  | supported | RW
41617 | W4 | 1 |  | supported | RW
41618 | V5 | 1 |  | supported | RW
41619 | W5 | 1 |  | supported | RW
41620 | V6 | 1 |  | supported | RW
41621 | W6 | 1 |  | supported | RW
41622 | V7 | 1 |  | supported | RW
41623 | W7 | 1 |  | supported | RW
41624 | V8 | 1 |  | supported | RW
41625 | W8 | 1 |  | supported | RW
41626 | V9 | 1 |  | supported | RW
41627 | W9 | 1 |  | supported | RW
41628 | V10 | 1 |  | supported | RW
41629 | W10 | 1 |  | supported | RW
41630 | V11 | 1 |  | unimplemented | RW
41631 | W11 | 1 |  | unimplemented | RW
41632 | V12 | 1 |  | unimplemented | RW
41633 | W12 | 1 |  | unimplemented | RW
41634 | V13 | 1 |  | unimplemented | RW
41635 | W13 | 1 |  | unimplemented | RW
41636 | V14 | 1 |  | unimplemented | RW
41637 | W14 | 1 |  | unimplemented | RW
41638 | V15 | 1 |  | unimplemented | RW
41639 | W15 | 1 |  | unimplemented | RW
41640 | V16 | 1 |  | unimplemented | RW
41641 | W16 | 1 |  | unimplemented | RW
41642 | V17 | 1 |  | unimplemented | RW
41643 | W17 | 1 |  | unimplemented | RW
41644 | V18 | 1 |  | unimplemented | RW
41645 | W18 | 1 |  | unimplemented | RW
41646 | V19 | 1 |  | unimplemented | RW
41647 | W19 | 1 |  | unimplemented | RW
41648 | V20 | 1 |  | unimplemented | RW
41649 | W20 | 1 |  | unimplemented | RW
41650 | CrvNam | 1 |  | unimplemented | RW
41658 | RmpPt1Tms | 1 |  | unimplemented | RW
41659 | RmpDecTmm | 1 |  | unimplemented | RW
41660 | RmpIncTmm | 1 |  | unimplemented | RW
41661 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
41662 | ActPt | 2 |  | supported | RW
41663 | DeptRef | 2 |  | supported | RW
41664 | V1 | 2 |  | supported | RW
41665 | W1 | 2 |  | supported | RW
41666 | V2 | 2 |  | supported | RW
41667 | W2 | 2 |  | supported | RW
41668 | V3 | 2 |  | supported | RW
41669 | W3 | 2 |  | supported | RW
41670 | V4 | 2 |  | supported | RW
41671 | W4 | 2 |  | supported | RW
41672 | V5 | 2 |  | supported | RW
41673 | W5 | 2 |  | supported | RW
41674 | V6 | 2 |  | supported | RW
41675 | W6 | 2 |  | supported | RW
41676 | V7 | 2 |  | supported | RW
41677 | W7 | 2 |  | supported | RW
41678 | V8 | 2 |  | supported | RW
41679 | W8 | 2 |  | supported | RW
41680 | V9 | 2 |  | supported | RW
41681 | W9 | 2 |  | supported | RW
41682 | V10 | 2 |  | supported | RW
41683 | W10 | 2 |  | supported | RW
41684 | V11 | 2 |  | unimplemented | RW
41685 | W11 | 2 |  | unimplemented | RW
41686 | V12 | 2 |  | unimplemented | RW
41687 | W12 | 2 |  | unimplemented | RW
41688 | V13 | 2 |  | unimplemented | RW
41689 | W13 | 2 |  | unimplemented | RW
41690 | V14 | 2 |  | unimplemented | RW
41691 | W14 | 2 |  | unimplemented | RW
41692 | V15 | 2 |  | unimplemented | RW
41693 | W15 | 2 |  | unimplemented | RW
41694 | V16 | 2 |  | unimplemented | RW
41695 | W16 | 2 |  | unimplemented | RW
41696 | V17 | 2 |  | unimplemented | RW
41697 | W17 | 2 |  | unimplemented | RW
41698 | V18 | 2 |  | unimplemented | RW
41699 | W18 | 2 |  | unimplemented | RW
41700 | V19 | 2 |  | unimplemented | RW
41701 | W19 | 2 |  | unimplemented | RW
41702 | V20 | 2 |  | unimplemented | RW
41703 | W20 | 2 |  | unimplemented | RW
41704 | CrvNam | 2 |  | unimplemented | RW
41712 | RmpPt1Tms | 2 |  | unimplemented | RW
41713 | RmpDecTmm | 2 |  | unimplemented | RW
41714 | RmpIncTmm | 2 |  | unimplemented | RW
41715 | ReadOnly | 2 |  | supported | R
41716 | ActPt | 3 |  | supported | RW
41717 | DeptRef | 3 |  | supported | RW
41718 | V1 | 3 |  | supported | RW
41719 | W1 | 3 |  | supported | RW
41720 | V2 | 3 |  | supported | RW
41721 | W2 | 3 |  | supported | RW
41722 | V3 | 3 |  | supported | RW
41723 | W3 | 3 |  | supported | RW
41724 | V4 | 3 |  | supported | RW
41725 | W4 | 3 |  | supported | RW
41726 | V5 | 3 |  | supported | RW
41727 | W5 | 3 |  | supported | RW
41728 | V6 | 3 |  | supported | RW
41729 | W6 | 3 |  | supported | RW
41730 | V7 | 3 |  | supported | RW
41731 | W7 | 3 |  | supported | RW
41732 | V8 | 3 |  | supported | RW
41733 | W8 | 3 |  | supported | RW
41734 | V9 | 3 |  | supported | RW
41735 | W9 | 3 |  | supported | RW
41736 | V10 | 3 |  | supported | RW
41737 | W10 | 3 |  | supported | RW
41738 | V11 | 3 |  | unimplemented | RW
41739 | W11 | 3 |  | unimplemented | RW
41740 | V12 | 3 |  | unimplemented | RW
41741 | W12 | 3 |  | unimplemented | RW
41742 | V13 | 3 |  | unimplemented | RW
41743 | W13 | 3 |  | unimplemented | RW
41744 | V14 | 3 |  | unimplemented | RW
41745 | W14 | 3 |  | unimplemented | RW
41746 | V15 | 3 |  | unimplemented | RW
41747 | W15 | 3 |  | unimplemented | RW
41748 | V16 | 3 |  | unimplemented | RW
41749 | W16 | 3 |  | unimplemented | RW
41750 | V17 | 3 |  | unimplemented | RW
41751 | W17 | 3 |  | unimplemented | RW
41752 | V18 | 3 |  | unimplemented | RW
41753 | W18 | 3 |  | unimplemented | RW
41754 | V19 | 3 |  | unimplemented | RW
41755 | W19 | 3 |  | unimplemented | RW
41756 | V20 | 3 |  | unimplemented | RW
41757 | W20 | 3 |  | unimplemented | RW
41758 | CrvNam | 3 |  | unimplemented | RW
41766 | RmpPt1Tms | 3 |  | unimplemented | RW
41767 | RmpDecTmm | 3 |  | unimplemented | RW
41768 | RmpIncTmm | 3 |  | unimplemented | RW
41769 | ReadOnly | 3 |  | supported | R
41770 | ActPt | 4 |  | supported | RW
41771 | DeptRef | 4 |  | supported | RW
41772 | V1 | 4 |  | supported | RW
41773 | W1 | 4 |  | supported | RW
41774 | V2 | 4 |  | supported | RW
41775 | W2 | 4 |  | supported | RW
41776 | V3 | 4 |  | supported | RW
41777 | W3 | 4 |  | supported | RW
41778 | V4 | 4 |  | supported | RW
41779 | W4 | 4 |  | supported | RW
41780 | V5 | 4 |  | supported | RW
41781 | W5 | 4 |  | supported | RW
41782 | V6 | 4 |  | supported | RW
41783 | W6 | 4 |  | supported | RW
41784 | V7 | 4 |  | supported | RW
41785 | W7 | 4 |  | supported | RW
41786 | V8 | 4 |  | supported | RW
41787 | W8 | 4 |  | supported | RW
41788 | V9 | 4 |  | supported | RW
41789 | W9 | 4 |  | supported | RW
41790 | V10 | 4 |  | supported | RW
41791 | W10 | 4 |  | supported | RW
41792 | V11 | 4 |  | unimplemented | RW
41793 | W11 | 4 |  | unimplemented | RW
41794 | V12 | 4 |  | unimplemented | RW
41795 | W12 | 4 |  | unimplemented | RW
41796 | V13 | 4 |  | unimplemented | RW
41797 | W13 | 4 |  | unimplemented | RW
41798 | V14 | 4 |  | unimplemented | RW
41799 | W14 | 4 |  | unimplemented | RW
41800 | V15 | 4 |  | unimplemented | RW
41801 | W15 | 4 |  | unimplemented | RW
41802 | V16 | 4 |  | unimplemented | RW
41803 | W16 | 4 |  | unimplemented | RW
41804 | V17 | 4 |  | unimplemented | RW
41805 | W17 | 4 |  | unimplemented | RW
41806 | V18 | 4 |  | unimplemented | RW
41807 | W18 | 4 |  | unimplemented | RW
41808 | V19 | 4 |  | unimplemented | RW
41809 | W19 | 4 |  | unimplemented | RW
41810 | V20 | 4 |  | unimplemented | RW
41811 | W20 | 4 |  | unimplemented | RW
41812 | CrvNam | 4 |  | unimplemented | RW
41820 | RmpPt1Tms | 4 |  | unimplemented | RW
41821 | RmpDecTmm | 4 |  | unimplemented | RW
41822 | RmpIncTmm | 4 |  | unimplemented | RW
41823 | ReadOnly | 4 |  | supported | R

## 134
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
41824 | ID |  |  | 134
41825 | L |  |  | 242
41826 | ActCrv |  |  | supported | RW
41827 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
41828 | WinTms |  |  | unimplemented | RW
41829 | RvrtTms |  |  | unimplemented | RW
41830 | RmpTms |  |  | unimplemented | RW
41831 | NCrv |  |  | supported | R
41832 | NPt |  |  | supported | R
41833 | Hz_SF |  |  | -2 | R
41834 | W_SF |  |  | -1 | R
41835 | RmpIncDec_SF |  |  | 0 | R
41836 | ActPt | 1 |  | supported | RW
41837 | Hz1 | 1 |  | supported | RW
41838 | W1 | 1 |  | supported | RW
41839 | Hz2 | 1 |  | supported | RW
41840 | W2 | 1 |  | supported | RW
41841 | Hz3 | 1 |  | supported | RW
41842 | W3 | 1 |  | supported | RW
41843 | Hz4 | 1 |  | supported | RW
41844 | W4 | 1 |  | supported | RW
41845 | Hz5 | 1 |  | supported | RW
41846 | W5 | 1 |  | supported | RW
41847 | Hz6 | 1 |  | supported | RW
41848 | W6 | 1 |  | supported | RW
41849 | Hz7 | 1 |  | supported | RW
41850 | W7 | 1 |  | supported | RW
41851 | Hz8 | 1 |  | supported | RW
41852 | W8 | 1 |  | supported | RW
41853 | Hz9 | 1 |  | supported | RW
41854 | W9 | 1 |  | supported | RW
41855 | Hz10 | 1 |  | supported | RW
41856 | W10 | 1 |  | supported | RW
41857 | Hz11 | 1 |  | unimplemented | RW
41858 | W11 | 1 |  | unimplemented | RW
41859 | Hz12 | 1 |  | unimplemented | RW
41860 | W12 | 1 |  | unimplemented | RW
41861 | Hz13 | 1 |  | unimplemented | RW
41862 | W13 | 1 |  | unimplemented | RW
41863 | Hz14 | 1 |  | unimplemented | RW
41864 | W14 | 1 |  | unimplemented | RW
41865 | Hz15 | 1 |  | unimplemented | RW
41866 | W15 | 1 |  | unimplemented | RW
41867 | Hz16 | 1 |  | unimplemented | RW
41868 | W16 | 1 |  | unimplemented | RW
41869 | Hz17 | 1 |  | unimplemented | RW
41870 | W17 | 1 |  | unimplemented | RW
41871 | Hz18 | 1 |  | unimplemented | RW
41872 | W18 | 1 |  | unimplemented | RW
41873 | Hz19 | 1 |  | unimplemented | RW
41874 | W19 | 1 |  | unimplemented | RW
41875 | Hz20 | 1 |  | unimplemented | RW
41876 | W20 | 1 |  | unimplemented | RW
41877 | CrvNam | 1 |  | unimplemented | RW
41885 | RmpPT1Tms | 1 |  | unimplemented | RW
41886 | RmpDecTmm | 1 |  | unimplemented | RW
41887 | RmpIncTmm | 1 |  | unimplemented | RW
41888 | RmpRsUp | 1 |  | unimplemented | RW
41889 | SnptW | 1 |  | unimplemented | RW
41890 | WRef | 1 |  | unimplemented | RW
41891 | WRefStrHz | 1 |  | unimplemented | RW
41892 | WRefStopHz | 1 |  | unimplemented | RW
41893 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
41894 | ActPt | 2 |  | supported | RW
41895 | Hz1 | 2 |  | supported | RW
41896 | W1 | 2 |  | supported | RW
41897 | Hz2 | 2 |  | supported | RW
41898 | W2 | 2 |  | supported | RW
41899 | Hz3 | 2 |  | supported | RW
41900 | W3 | 2 |  | supported | RW
41901 | Hz4 | 2 |  | supported | RW
41902 | W4 | 2 |  | supported | RW
41903 | Hz5 | 2 |  | supported | RW
41904 | W5 | 2 |  | supported | RW
41905 | Hz6 | 2 |  | supported | RW
41906 | W6 | 2 |  | supported | RW
41907 | Hz7 | 2 |  | supported | RW
41908 | W7 | 2 |  | supported | RW
41909 | Hz8 | 2 |  | supported | RW
41910 | W8 | 2 |  | supported | RW
41911 | Hz9 | 2 |  | supported | RW
41912 | W9 | 2 |  | supported | RW
41913 | Hz10 | 2 |  | supported | RW
41914 | W10 | 2 |  | supported | RW
41915 | Hz11 | 2 |  | unimplemented | RW
41916 | W11 | 2 |  | unimplemented | RW
41917 | Hz12 | 2 |  | unimplemented | RW
41918 | W12 | 2 |  | unimplemented | RW
41919 | Hz13 | 2 |  | unimplemented | RW
41920 | W13 | 2 |  | unimplemented | RW
41921 | Hz14 | 2 |  | unimplemented | RW
41922 | W14 | 2 |  | unimplemented | RW
41923 | Hz15 | 2 |  | unimplemented | RW
41924 | W15 | 2 |  | unimplemented | RW
41925 | Hz16 | 2 |  | unimplemented | RW
41926 | W16 | 2 |  | unimplemented | RW
41927 | Hz17 | 2 |  | unimplemented | RW
41928 | W17 | 2 |  | unimplemented | RW
41929 | Hz18 | 2 |  | unimplemented | RW
41930 | W18 | 2 |  | unimplemented | RW
41931 | Hz19 | 2 |  | unimplemented | RW
41932 | W19 | 2 |  | unimplemented | RW
41933 | Hz20 | 2 |  | unimplemented | RW
41934 | W20 | 2 |  | unimplemented | RW
41935 | CrvNam | 2 |  | unimplemented | RW
41943 | RmpPT1Tms | 2 |  | unimplemented | RW
41944 | RmpDecTmm | 2 |  | unimplemented | RW
41945 | RmpIncTmm | 2 |  | unimplemented | RW
41946 | RmpRsUp | 2 |  | unimplemented | RW
41947 | SnptW | 2 |  | unimplemented | RW
41948 | WRef | 2 |  | unimplemented | RW
41949 | WRefStrHz | 2 |  | unimplemented | RW
41950 | WRefStopHz | 2 |  | unimplemented | RW
41951 | ReadOnly | 2 |  | supported | R
41952 | ActPt | 3 |  | supported | RW
41953 | Hz1 | 3 |  | supported | RW
41954 | W1 | 3 |  | supported | RW
41955 | Hz2 | 3 |  | supported | RW
41956 | W2 | 3 |  | supported | RW
41957 | Hz3 | 3 |  | supported | RW
41958 | W3 | 3 |  | supported | RW
41959 | Hz4 | 3 |  | supported | RW
41960 | W4 | 3 |  | supported | RW
41961 | Hz5 | 3 |  | supported | RW
41962 | W5 | 3 |  | supported | RW
41963 | Hz6 | 3 |  | supported | RW
41964 | W6 | 3 |  | supported | RW
41965 | Hz7 | 3 |  | supported | RW
41966 | W7 | 3 |  | supported | RW
41967 | Hz8 | 3 |  | supported | RW
41968 | W8 | 3 |  | supported | RW
41969 | Hz9 | 3 |  | supported | RW
41970 | W9 | 3 |  | supported | RW
41971 | Hz10 | 3 |  | supported | RW
41972 | W10 | 3 |  | supported | RW
41973 | Hz11 | 3 |  | unimplemented | RW
41974 | W11 | 3 |  | unimplemented | RW
41975 | Hz12 | 3 |  | unimplemented | RW
41976 | W12 | 3 |  | unimplemented | RW
41977 | Hz13 | 3 |  | unimplemented | RW
41978 | W13 | 3 |  | unimplemented | RW
41979 | Hz14 | 3 |  | unimplemented | RW
41980 | W14 | 3 |  | unimplemented | RW
41981 | Hz15 | 3 |  | unimplemented | RW
41982 | W15 | 3 |  | unimplemented | RW
41983 | Hz16 | 3 |  | unimplemented | RW
41984 | W16 | 3 |  | unimplemented | RW
41985 | Hz17 | 3 |  | unimplemented | RW
41986 | W17 | 3 |  | unimplemented | RW
41987 | Hz18 | 3 |  | unimplemented | RW
41988 | W18 | 3 |  | unimplemented | RW
41989 | Hz19 | 3 |  | unimplemented | RW
41990 | W19 | 3 |  | unimplemented | RW
41991 | Hz20 | 3 |  | unimplemented | RW
41992 | W20 | 3 |  | unimplemented | RW
41993 | CrvNam | 3 |  | unimplemented | RW
42001 | RmpPT1Tms | 3 |  | unimplemented | RW
42002 | RmpDecTmm | 3 |  | unimplemented | RW
42003 | RmpIncTmm | 3 |  | unimplemented | RW
42004 | RmpRsUp | 3 |  | unimplemented | RW
42005 | SnptW | 3 |  | unimplemented | RW
42006 | WRef | 3 |  | unimplemented | RW
42007 | WRefStrHz | 3 |  | unimplemented | RW
42008 | WRefStopHz | 3 |  | unimplemented | RW
42009 | ReadOnly | 3 |  | supported | R
42010 | ActPt | 4 |  | supported | RW
42011 | Hz1 | 4 |  | supported | RW
42012 | W1 | 4 |  | supported | RW
42013 | Hz2 | 4 |  | supported | RW
42014 | W2 | 4 |  | supported | RW
42015 | Hz3 | 4 |  | supported | RW
42016 | W3 | 4 |  | supported | RW
42017 | Hz4 | 4 |  | supported | RW
42018 | W4 | 4 |  | supported | RW
42019 | Hz5 | 4 |  | supported | RW
42020 | W5 | 4 |  | supported | RW
42021 | Hz6 | 4 |  | supported | RW
42022 | W6 | 4 |  | supported | RW
42023 | Hz7 | 4 |  | supported | RW
42024 | W7 | 4 |  | supported | RW
42025 | Hz8 | 4 |  | supported | RW
42026 | W8 | 4 |  | supported | RW
42027 | Hz9 | 4 |  | supported | RW
42028 | W9 | 4 |  | supported | RW
42029 | Hz10 | 4 |  | supported | RW
42030 | W10 | 4 |  | supported | RW
42031 | Hz11 | 4 |  | unimplemented | RW
42032 | W11 | 4 |  | unimplemented | RW
42033 | Hz12 | 4 |  | unimplemented | RW
42034 | W12 | 4 |  | unimplemented | RW
42035 | Hz13 | 4 |  | unimplemented | RW
42036 | W13 | 4 |  | unimplemented | RW
42037 | Hz14 | 4 |  | unimplemented | RW
42038 | W14 | 4 |  | unimplemented | RW
42039 | Hz15 | 4 |  | unimplemented | RW
42040 | W15 | 4 |  | unimplemented | RW
42041 | Hz16 | 4 |  | unimplemented | RW
42042 | W16 | 4 |  | unimplemented | RW
42043 | Hz17 | 4 |  | unimplemented | RW
42044 | W17 | 4 |  | unimplemented | RW
42045 | Hz18 | 4 |  | unimplemented | RW
42046 | W18 | 4 |  | unimplemented | RW
42047 | Hz19 | 4 |  | unimplemented | RW
42048 | W19 | 4 |  | unimplemented | RW
42049 | Hz20 | 4 |  | unimplemented | RW
42050 | W20 | 4 |  | unimplemented | RW
42051 | CrvNam | 4 |  | unimplemented | RW
42059 | RmpPT1Tms | 4 |  | unimplemented | RW
42060 | RmpDecTmm | 4 |  | unimplemented | RW
42061 | RmpIncTmm | 4 |  | unimplemented | RW
42062 | RmpRsUp | 4 |  | unimplemented | RW
42063 | SnptW | 4 |  | unimplemented | RW
42064 | WRef | 4 |  | unimplemented | RW
42065 | WRefStrHz | 4 |  | unimplemented | RW
42066 | WRefStopHz | 4 |  | unimplemented | RW
42067 | ReadOnly | 4 |  | supported | R

## 64235
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
42068 | ID |  |  | 64235
42069 | L |  |  | 370
42070 | ActCrv |  |  | supported | RW
42071 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
42072 | WinTms |  |  | unimplemented | RW
42073 | RvrtTms |  |  | unimplemented | RW
42074 | RmpTms |  |  | unimplemented | RW
42075 | NCrv |  |  | supported | R
42076 | NPt |  |  | supported | R
42077 | Tms_SF |  |  | -6 | R
42078 | Hz_SF |  |  | -2 | R
42079 | Pad |  |  |  | R
42080 | ActPt | 1 |  | supported | RW
42081 | Tms1 | 1 |  | supported | RW
42083 | Hz1 | 1 |  | supported | RW
42084 | Fn1 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42085 | Tms2 | 1 |  | supported | RW
42087 | Hz2 | 1 |  | supported | RW
42088 | Fn2 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42089 | Tms3 | 1 |  | supported | RW
42091 | Hz3 | 1 |  | supported | RW
42092 | Fn3 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42093 | Tms4 | 1 |  | supported | RW
42095 | Hz4 | 1 |  | supported | RW
42096 | Fn4 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42097 | Tms5 | 1 |  | supported | RW
42099 | Hz5 | 1 |  | supported | RW
42100 | Fn5 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42101 | Tms6 | 1 |  | supported | RW
42103 | Hz6 | 1 |  | supported | RW
42104 | Fn6 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42105 | Tms7 | 1 |  | supported | RW
42107 | Hz7 | 1 |  | supported | RW
42108 | Fn7 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42109 | Tms8 | 1 |  | supported | RW
42111 | Hz8 | 1 |  | supported | RW
42112 | Fn8 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42113 | Tms9 | 1 |  | supported | RW
42115 | Hz9 | 1 |  | supported | RW
42116 | Fn9 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42117 | Tms10 | 1 |  | supported | RW
42119 | Hz10 | 1 |  | supported | RW
42120 | Fn10 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42121 | Tms11 | 1 |  | unimplemented | RW
42123 | Hz11 | 1 |  | unimplemented | RW
42124 | Fn11 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42125 | Tms12 | 1 |  | unimplemented | RW
42127 | Hz12 | 1 |  | unimplemented | RW
42128 | Fn12 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42129 | Tms13 | 1 |  | unimplemented | RW
42131 | Hz13 | 1 |  | unimplemented | RW
42132 | Fn13 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42133 | Tms14 | 1 |  | unimplemented | RW
42135 | Hz14 | 1 |  | unimplemented | RW
42136 | Fn14 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42137 | Tms15 | 1 |  | unimplemented | RW
42139 | Hz15 | 1 |  | unimplemented | RW
42140 | Fn15 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42141 | Tms16 | 1 |  | unimplemented | RW
42143 | Hz16 | 1 |  | unimplemented | RW
42144 | Fn16 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42145 | Tms17 | 1 |  | unimplemented | RW
42147 | Hz17 | 1 |  | unimplemented | RW
42148 | Fn17 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42149 | Tms18 | 1 |  | unimplemented | RW
42151 | Hz18 | 1 |  | unimplemented | RW
42152 | Fn18 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42153 | Tms19 | 1 |  | unimplemented | RW
42155 | Hz19 | 1 |  | unimplemented | RW
42156 | Fn19 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42157 | Tms20 | 1 |  | unimplemented | RW
42159 | Hz20 | 1 |  | unimplemented | RW
42160 | Fn20 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42161 | CrvNam | 1 |  | unimplemented | RW
42169 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
42170 | ActPt | 2 |  | supported | RW
42171 | Tms1 | 2 |  | supported | RW
42173 | Hz1 | 2 |  | supported | RW
42174 | Fn1 | 2 |  | supported | RW
42175 | Tms2 | 2 |  | supported | RW
42177 | Hz2 | 2 |  | supported | RW
42178 | Fn2 | 2 |  | supported | RW
42179 | Tms3 | 2 |  | supported | RW
42181 | Hz3 | 2 |  | supported | RW
42182 | Fn3 | 2 |  | supported | RW
42183 | Tms4 | 2 |  | supported | RW
42185 | Hz4 | 2 |  | supported | RW
42186 | Fn4 | 2 |  | supported | RW
42187 | Tms5 | 2 |  | supported | RW
42189 | Hz5 | 2 |  | supported | RW
42190 | Fn5 | 2 |  | supported | RW
42191 | Tms6 | 2 |  | supported | RW
42193 | Hz6 | 2 |  | supported | RW
42194 | Fn6 | 2 |  | supported | RW
42195 | Tms7 | 2 |  | supported | RW
42197 | Hz7 | 2 |  | supported | RW
42198 | Fn7 | 2 |  | supported | RW
42199 | Tms8 | 2 |  | supported | RW
42201 | Hz8 | 2 |  | supported | RW
42202 | Fn8 | 2 |  | supported | RW
42203 | Tms9 | 2 |  | supported | RW
42205 | Hz9 | 2 |  | supported | RW
42206 | Fn9 | 2 |  | supported | RW
42207 | Tms10 | 2 |  | supported | RW
42209 | Hz10 | 2 |  | supported | RW
42210 | Fn10 | 2 |  | supported | RW
42211 | Tms11 | 2 |  | unimplemented | RW
42213 | Hz11 | 2 |  | unimplemented | RW
42214 | Fn11 | 2 |  | unimplemented | RW
42215 | Tms12 | 2 |  | unimplemented | RW
42217 | Hz12 | 2 |  | unimplemented | RW
42218 | Fn12 | 2 |  | unimplemented | RW
42219 | Tms13 | 2 |  | unimplemented | RW
42221 | Hz13 | 2 |  | unimplemented | RW
42222 | Fn13 | 2 |  | unimplemented | RW
42223 | Tms14 | 2 |  | unimplemented | RW
42225 | Hz14 | 2 |  | unimplemented | RW
42226 | Fn14 | 2 |  | unimplemented | RW
42227 | Tms15 | 2 |  | unimplemented | RW
42229 | Hz15 | 2 |  | unimplemented | RW
42230 | Fn15 | 2 |  | unimplemented | RW
42231 | Tms16 | 2 |  | unimplemented | RW
42233 | Hz16 | 2 |  | unimplemented | RW
42234 | Fn16 | 2 |  | unimplemented | RW
42235 | Tms17 | 2 |  | unimplemented | RW
42237 | Hz17 | 2 |  | unimplemented | RW
42238 | Fn17 | 2 |  | unimplemented | RW
42239 | Tms18 | 2 |  | unimplemented | RW
42241 | Hz18 | 2 |  | unimplemented | RW
42242 | Fn18 | 2 |  | unimplemented | RW
42243 | Tms19 | 2 |  | unimplemented | RW
42245 | Hz19 | 2 |  | unimplemented | RW
42246 | Fn19 | 2 |  | unimplemented | RW
42247 | Tms20 | 2 |  | unimplemented | RW
42249 | Hz20 | 2 |  | unimplemented | RW
42250 | Fn20 | 2 |  | unimplemented | RW
42251 | CrvNam | 2 |  | unimplemented | RW
42259 | ReadOnly | 2 |  | supported | R
42260 | ActPt | 3 |  | supported | RW
42261 | Tms1 | 3 |  | supported | RW
42263 | Hz1 | 3 |  | supported | RW
42264 | Fn1 | 3 |  | supported | RW
42265 | Tms2 | 3 |  | supported | RW
42267 | Hz2 | 3 |  | supported | RW
42268 | Fn2 | 3 |  | supported | RW
42269 | Tms3 | 3 |  | supported | RW
42271 | Hz3 | 3 |  | supported | RW
42272 | Fn3 | 3 |  | supported | RW
42273 | Tms4 | 3 |  | supported | RW
42275 | Hz4 | 3 |  | supported | RW
42276 | Fn4 | 3 |  | supported | RW
42277 | Tms5 | 3 |  | supported | RW
42279 | Hz5 | 3 |  | supported | RW
42280 | Fn5 | 3 |  | supported | RW
42281 | Tms6 | 3 |  | supported | RW
42283 | Hz6 | 3 |  | supported | RW
42284 | Fn6 | 3 |  | supported | RW
42285 | Tms7 | 3 |  | supported | RW
42287 | Hz7 | 3 |  | supported | RW
42288 | Fn7 | 3 |  | supported | RW
42289 | Tms8 | 3 |  | supported | RW
42291 | Hz8 | 3 |  | supported | RW
42292 | Fn8 | 3 |  | supported | RW
42293 | Tms9 | 3 |  | supported | RW
42295 | Hz9 | 3 |  | supported | RW
42296 | Fn9 | 3 |  | supported | RW
42297 | Tms10 | 3 |  | supported | RW
42299 | Hz10 | 3 |  | supported | RW
42300 | Fn10 | 3 |  | supported | RW
42301 | Tms11 | 3 |  | unimplemented | RW
42303 | Hz11 | 3 |  | unimplemented | RW
42304 | Fn11 | 3 |  | unimplemented | RW
42305 | Tms12 | 3 |  | unimplemented | RW
42307 | Hz12 | 3 |  | unimplemented | RW
42308 | Fn12 | 3 |  | unimplemented | RW
42309 | Tms13 | 3 |  | unimplemented | RW
42311 | Hz13 | 3 |  | unimplemented | RW
42312 | Fn13 | 3 |  | unimplemented | RW
42313 | Tms14 | 3 |  | unimplemented | RW
42315 | Hz14 | 3 |  | unimplemented | RW
42316 | Fn14 | 3 |  | unimplemented | RW
42317 | Tms15 | 3 |  | unimplemented | RW
42319 | Hz15 | 3 |  | unimplemented | RW
42320 | Fn15 | 3 |  | unimplemented | RW
42321 | Tms16 | 3 |  | unimplemented | RW
42323 | Hz16 | 3 |  | unimplemented | RW
42324 | Fn16 | 3 |  | unimplemented | RW
42325 | Tms17 | 3 |  | unimplemented | RW
42327 | Hz17 | 3 |  | unimplemented | RW
42328 | Fn17 | 3 |  | unimplemented | RW
42329 | Tms18 | 3 |  | unimplemented | RW
42331 | Hz18 | 3 |  | unimplemented | RW
42332 | Fn18 | 3 |  | unimplemented | RW
42333 | Tms19 | 3 |  | unimplemented | RW
42335 | Hz19 | 3 |  | unimplemented | RW
42336 | Fn19 | 3 |  | unimplemented | RW
42337 | Tms20 | 3 |  | unimplemented | RW
42339 | Hz20 | 3 |  | unimplemented | RW
42340 | Fn20 | 3 |  | unimplemented | RW
42341 | CrvNam | 3 |  | unimplemented | RW
42349 | ReadOnly | 3 |  | supported | R
42350 | ActPt | 4 |  | supported | RW
42351 | Tms1 | 4 |  | supported | RW
42353 | Hz1 | 4 |  | supported | RW
42354 | Fn1 | 4 |  | supported | RW
42355 | Tms2 | 4 |  | supported | RW
42357 | Hz2 | 4 |  | supported | RW
42358 | Fn2 | 4 |  | supported | RW
42359 | Tms3 | 4 |  | supported | RW
42361 | Hz3 | 4 |  | supported | RW
42362 | Fn3 | 4 |  | supported | RW
42363 | Tms4 | 4 |  | supported | RW
42365 | Hz4 | 4 |  | supported | RW
42366 | Fn4 | 4 |  | supported | RW
42367 | Tms5 | 4 |  | supported | RW
42369 | Hz5 | 4 |  | supported | RW
42370 | Fn5 | 4 |  | supported | RW
42371 | Tms6 | 4 |  | supported | RW
42373 | Hz6 | 4 |  | supported | RW
42374 | Fn6 | 4 |  | supported | RW
42375 | Tms7 | 4 |  | supported | RW
42377 | Hz7 | 4 |  | supported | RW
42378 | Fn7 | 4 |  | supported | RW
42379 | Tms8 | 4 |  | supported | RW
42381 | Hz8 | 4 |  | supported | RW
42382 | Fn8 | 4 |  | supported | RW
42383 | Tms9 | 4 |  | supported | RW
42385 | Hz9 | 4 |  | supported | RW
42386 | Fn9 | 4 |  | supported | RW
42387 | Tms10 | 4 |  | supported | RW
42389 | Hz10 | 4 |  | supported | RW
42390 | Fn10 | 4 |  | supported | RW
42391 | Tms11 | 4 |  | unimplemented | RW
42393 | Hz11 | 4 |  | unimplemented | RW
42394 | Fn11 | 4 |  | unimplemented | RW
42395 | Tms12 | 4 |  | unimplemented | RW
42397 | Hz12 | 4 |  | unimplemented | RW
42398 | Fn12 | 4 |  | unimplemented | RW
42399 | Tms13 | 4 |  | unimplemented | RW
42401 | Hz13 | 4 |  | unimplemented | RW
42402 | Fn13 | 4 |  | unimplemented | RW
42403 | Tms14 | 4 |  | unimplemented | RW
42405 | Hz14 | 4 |  | unimplemented | RW
42406 | Fn14 | 4 |  | unimplemented | RW
42407 | Tms15 | 4 |  | unimplemented | RW
42409 | Hz15 | 4 |  | unimplemented | RW
42410 | Fn15 | 4 |  | unimplemented | RW
42411 | Tms16 | 4 |  | unimplemented | RW
42413 | Hz16 | 4 |  | unimplemented | RW
42414 | Fn16 | 4 |  | unimplemented | RW
42415 | Tms17 | 4 |  | unimplemented | RW
42417 | Hz17 | 4 |  | unimplemented | RW
42418 | Fn17 | 4 |  | unimplemented | RW
42419 | Tms18 | 4 |  | unimplemented | RW
42421 | Hz18 | 4 |  | unimplemented | RW
42422 | Fn18 | 4 |  | unimplemented | RW
42423 | Tms19 | 4 |  | unimplemented | RW
42425 | Hz19 | 4 |  | unimplemented | RW
42426 | Fn19 | 4 |  | unimplemented | RW
42427 | Tms20 | 4 |  | unimplemented | RW
42429 | Hz20 | 4 |  | unimplemented | RW
42430 | Fn20 | 4 |  | unimplemented | RW
42431 | CrvNam | 4 |  | unimplemented | RW
42439 | ReadOnly | 4 |  | supported | R

## 64236
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
42440 | ID |  |  | 64236
42441 | L |  |  | 370
42442 | ActCrv |  |  | supported | RW
42443 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
42444 | WinTms |  |  | unimplemented | RW
42445 | RvrtTms |  |  | unimplemented | RW
42446 | RmpTms |  |  | unimplemented | RW
42447 | NCrv |  |  | supported | R
42448 | NPt |  |  | supported | R
42449 | Tms_SF |  |  | -6 | R
42450 | Hz_SF |  |  | -2 | R
42451 | Pad |  |  |  | R
42452 | ActPt | 1 |  | supported | RW
42453 | Tms1 | 1 |  | supported | RW
42455 | Hz1 | 1 |  | supported | RW
42456 | Fn1 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42457 | Tms2 | 1 |  | supported | RW
42459 | Hz2 | 1 |  | supported | RW
42460 | Fn2 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42461 | Tms3 | 1 |  | supported | RW
42463 | Hz3 | 1 |  | supported | RW
42464 | Fn3 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42465 | Tms4 | 1 |  | supported | RW
42467 | Hz4 | 1 |  | supported | RW
42468 | Fn4 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42469 | Tms5 | 1 |  | supported | RW
42471 | Hz5 | 1 |  | supported | RW
42472 | Fn5 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42473 | Tms6 | 1 |  | supported | RW
42475 | Hz6 | 1 |  | supported | RW
42476 | Fn6 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42477 | Tms7 | 1 |  | supported | RW
42479 | Hz7 | 1 |  | supported | RW
42480 | Fn7 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42481 | Tms8 | 1 |  | supported | RW
42483 | Hz8 | 1 |  | supported | RW
42484 | Fn8 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42485 | Tms9 | 1 |  | supported | RW
42487 | Hz9 | 1 |  | supported | RW
42488 | Fn9 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42489 | Tms10 | 1 |  | supported | RW
42491 | Hz10 | 1 |  | supported | RW
42492 | Fn10 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42493 | Tms11 | 1 |  | unimplemented | RW
42495 | Hz11 | 1 |  | unimplemented | RW
42496 | Fn11 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42497 | Tms12 | 1 |  | unimplemented | RW
42499 | Hz12 | 1 |  | unimplemented | RW
42500 | Fn12 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42501 | Tms13 | 1 |  | unimplemented | RW
42503 | Hz13 | 1 |  | unimplemented | RW
42504 | Fn13 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42505 | Tms14 | 1 |  | unimplemented | RW
42507 | Hz14 | 1 |  | unimplemented | RW
42508 | Fn14 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42509 | Tms15 | 1 |  | unimplemented | RW
42511 | Hz15 | 1 |  | unimplemented | RW
42512 | Fn15 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42513 | Tms16 | 1 |  | unimplemented | RW
42515 | Hz16 | 1 |  | unimplemented | RW
42516 | Fn16 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42517 | Tms17 | 1 |  | unimplemented | RW
42519 | Hz17 | 1 |  | unimplemented | RW
42520 | Fn17 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42521 | Tms18 | 1 |  | unimplemented | RW
42523 | Hz18 | 1 |  | unimplemented | RW
42524 | Fn18 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42525 | Tms19 | 1 |  | unimplemented | RW
42527 | Hz19 | 1 |  | unimplemented | RW
42528 | Fn19 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42529 | Tms20 | 1 |  | unimplemented | RW
42531 | Hz20 | 1 |  | unimplemented | RW
42532 | Fn20 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42533 | CrvNam | 1 |  | unimplemented | RW
42541 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
42542 | ActPt | 2 |  | supported | RW
42543 | Tms1 | 2 |  | supported | RW
42545 | Hz1 | 2 |  | supported | RW
42546 | Fn1 | 2 |  | supported | RW
42547 | Tms2 | 2 |  | supported | RW
42549 | Hz2 | 2 |  | supported | RW
42550 | Fn2 | 2 |  | supported | RW
42551 | Tms3 | 2 |  | supported | RW
42553 | Hz3 | 2 |  | supported | RW
42554 | Fn3 | 2 |  | supported | RW
42555 | Tms4 | 2 |  | supported | RW
42557 | Hz4 | 2 |  | supported | RW
42558 | Fn4 | 2 |  | supported | RW
42559 | Tms5 | 2 |  | supported | RW
42561 | Hz5 | 2 |  | supported | RW
42562 | Fn5 | 2 |  | supported | RW
42563 | Tms6 | 2 |  | supported | RW
42565 | Hz6 | 2 |  | supported | RW
42566 | Fn6 | 2 |  | supported | RW
42567 | Tms7 | 2 |  | supported | RW
42569 | Hz7 | 2 |  | supported | RW
42570 | Fn7 | 2 |  | supported | RW
42571 | Tms8 | 2 |  | supported | RW
42573 | Hz8 | 2 |  | supported | RW
42574 | Fn8 | 2 |  | supported | RW
42575 | Tms9 | 2 |  | supported | RW
42577 | Hz9 | 2 |  | supported | RW
42578 | Fn9 | 2 |  | supported | RW
42579 | Tms10 | 2 |  | supported | RW
42581 | Hz10 | 2 |  | supported | RW
42582 | Fn10 | 2 |  | supported | RW
42583 | Tms11 | 2 |  | unimplemented | RW
42585 | Hz11 | 2 |  | unimplemented | RW
42586 | Fn11 | 2 |  | unimplemented | RW
42587 | Tms12 | 2 |  | unimplemented | RW
42589 | Hz12 | 2 |  | unimplemented | RW
42590 | Fn12 | 2 |  | unimplemented | RW
42591 | Tms13 | 2 |  | unimplemented | RW
42593 | Hz13 | 2 |  | unimplemented | RW
42594 | Fn13 | 2 |  | unimplemented | RW
42595 | Tms14 | 2 |  | unimplemented | RW
42597 | Hz14 | 2 |  | unimplemented | RW
42598 | Fn14 | 2 |  | unimplemented | RW
42599 | Tms15 | 2 |  | unimplemented | RW
42601 | Hz15 | 2 |  | unimplemented | RW
42602 | Fn15 | 2 |  | unimplemented | RW
42603 | Tms16 | 2 |  | unimplemented | RW
42605 | Hz16 | 2 |  | unimplemented | RW
42606 | Fn16 | 2 |  | unimplemented | RW
42607 | Tms17 | 2 |  | unimplemented | RW
42609 | Hz17 | 2 |  | unimplemented | RW
42610 | Fn17 | 2 |  | unimplemented | RW
42611 | Tms18 | 2 |  | unimplemented | RW
42613 | Hz18 | 2 |  | unimplemented | RW
42614 | Fn18 | 2 |  | unimplemented | RW
42615 | Tms19 | 2 |  | unimplemented | RW
42617 | Hz19 | 2 |  | unimplemented | RW
42618 | Fn19 | 2 |  | unimplemented | RW
42619 | Tms20 | 2 |  | unimplemented | RW
42621 | Hz20 | 2 |  | unimplemented | RW
42622 | Fn20 | 2 |  | unimplemented | RW
42623 | CrvNam | 2 |  | unimplemented | RW
42631 | ReadOnly | 2 |  | supported | R
42632 | ActPt | 3 |  | supported | RW
42633 | Tms1 | 3 |  | supported | RW
42635 | Hz1 | 3 |  | supported | RW
42636 | Fn1 | 3 |  | supported | RW
42637 | Tms2 | 3 |  | supported | RW
42639 | Hz2 | 3 |  | supported | RW
42640 | Fn2 | 3 |  | supported | RW
42641 | Tms3 | 3 |  | supported | RW
42643 | Hz3 | 3 |  | supported | RW
42644 | Fn3 | 3 |  | supported | RW
42645 | Tms4 | 3 |  | supported | RW
42647 | Hz4 | 3 |  | supported | RW
42648 | Fn4 | 3 |  | supported | RW
42649 | Tms5 | 3 |  | supported | RW
42651 | Hz5 | 3 |  | supported | RW
42652 | Fn5 | 3 |  | supported | RW
42653 | Tms6 | 3 |  | supported | RW
42655 | Hz6 | 3 |  | supported | RW
42656 | Fn6 | 3 |  | supported | RW
42657 | Tms7 | 3 |  | supported | RW
42659 | Hz7 | 3 |  | supported | RW
42660 | Fn7 | 3 |  | supported | RW
42661 | Tms8 | 3 |  | supported | RW
42663 | Hz8 | 3 |  | supported | RW
42664 | Fn8 | 3 |  | supported | RW
42665 | Tms9 | 3 |  | supported | RW
42667 | Hz9 | 3 |  | supported | RW
42668 | Fn9 | 3 |  | supported | RW
42669 | Tms10 | 3 |  | supported | RW
42671 | Hz10 | 3 |  | supported | RW
42672 | Fn10 | 3 |  | supported | RW
42673 | Tms11 | 3 |  | unimplemented | RW
42675 | Hz11 | 3 |  | unimplemented | RW
42676 | Fn11 | 3 |  | unimplemented | RW
42677 | Tms12 | 3 |  | unimplemented | RW
42679 | Hz12 | 3 |  | unimplemented | RW
42680 | Fn12 | 3 |  | unimplemented | RW
42681 | Tms13 | 3 |  | unimplemented | RW
42683 | Hz13 | 3 |  | unimplemented | RW
42684 | Fn13 | 3 |  | unimplemented | RW
42685 | Tms14 | 3 |  | unimplemented | RW
42687 | Hz14 | 3 |  | unimplemented | RW
42688 | Fn14 | 3 |  | unimplemented | RW
42689 | Tms15 | 3 |  | unimplemented | RW
42691 | Hz15 | 3 |  | unimplemented | RW
42692 | Fn15 | 3 |  | unimplemented | RW
42693 | Tms16 | 3 |  | unimplemented | RW
42695 | Hz16 | 3 |  | unimplemented | RW
42696 | Fn16 | 3 |  | unimplemented | RW
42697 | Tms17 | 3 |  | unimplemented | RW
42699 | Hz17 | 3 |  | unimplemented | RW
42700 | Fn17 | 3 |  | unimplemented | RW
42701 | Tms18 | 3 |  | unimplemented | RW
42703 | Hz18 | 3 |  | unimplemented | RW
42704 | Fn18 | 3 |  | unimplemented | RW
42705 | Tms19 | 3 |  | unimplemented | RW
42707 | Hz19 | 3 |  | unimplemented | RW
42708 | Fn19 | 3 |  | unimplemented | RW
42709 | Tms20 | 3 |  | unimplemented | RW
42711 | Hz20 | 3 |  | unimplemented | RW
42712 | Fn20 | 3 |  | unimplemented | RW
42713 | CrvNam | 3 |  | unimplemented | RW
42721 | ReadOnly | 3 |  | supported | R
42722 | ActPt | 4 |  | supported | RW
42723 | Tms1 | 4 |  | supported | RW
42725 | Hz1 | 4 |  | supported | RW
42726 | Fn1 | 4 |  | supported | RW
42727 | Tms2 | 4 |  | supported | RW
42729 | Hz2 | 4 |  | supported | RW
42730 | Fn2 | 4 |  | supported | RW
42731 | Tms3 | 4 |  | supported | RW
42733 | Hz3 | 4 |  | supported | RW
42734 | Fn3 | 4 |  | supported | RW
42735 | Tms4 | 4 |  | supported | RW
42737 | Hz4 | 4 |  | supported | RW
42738 | Fn4 | 4 |  | supported | RW
42739 | Tms5 | 4 |  | supported | RW
42741 | Hz5 | 4 |  | supported | RW
42742 | Fn5 | 4 |  | supported | RW
42743 | Tms6 | 4 |  | supported | RW
42745 | Hz6 | 4 |  | supported | RW
42746 | Fn6 | 4 |  | supported | RW
42747 | Tms7 | 4 |  | supported | RW
42749 | Hz7 | 4 |  | supported | RW
42750 | Fn7 | 4 |  | supported | RW
42751 | Tms8 | 4 |  | supported | RW
42753 | Hz8 | 4 |  | supported | RW
42754 | Fn8 | 4 |  | supported | RW
42755 | Tms9 | 4 |  | supported | RW
42757 | Hz9 | 4 |  | supported | RW
42758 | Fn9 | 4 |  | supported | RW
42759 | Tms10 | 4 |  | supported | RW
42761 | Hz10 | 4 |  | supported | RW
42762 | Fn10 | 4 |  | supported | RW
42763 | Tms11 | 4 |  | unimplemented | RW
42765 | Hz11 | 4 |  | unimplemented | RW
42766 | Fn11 | 4 |  | unimplemented | RW
42767 | Tms12 | 4 |  | unimplemented | RW
42769 | Hz12 | 4 |  | unimplemented | RW
42770 | Fn12 | 4 |  | unimplemented | RW
42771 | Tms13 | 4 |  | unimplemented | RW
42773 | Hz13 | 4 |  | unimplemented | RW
42774 | Fn13 | 4 |  | unimplemented | RW
42775 | Tms14 | 4 |  | unimplemented | RW
42777 | Hz14 | 4 |  | unimplemented | RW
42778 | Fn14 | 4 |  | unimplemented | RW
42779 | Tms15 | 4 |  | unimplemented | RW
42781 | Hz15 | 4 |  | unimplemented | RW
42782 | Fn15 | 4 |  | unimplemented | RW
42783 | Tms16 | 4 |  | unimplemented | RW
42785 | Hz16 | 4 |  | unimplemented | RW
42786 | Fn16 | 4 |  | unimplemented | RW
42787 | Tms17 | 4 |  | unimplemented | RW
42789 | Hz17 | 4 |  | unimplemented | RW
42790 | Fn17 | 4 |  | unimplemented | RW
42791 | Tms18 | 4 |  | unimplemented | RW
42793 | Hz18 | 4 |  | unimplemented | RW
42794 | Fn18 | 4 |  | unimplemented | RW
42795 | Tms19 | 4 |  | unimplemented | RW
42797 | Hz19 | 4 |  | unimplemented | RW
42798 | Fn19 | 4 |  | unimplemented | RW
42799 | Tms20 | 4 |  | unimplemented | RW
42801 | Hz20 | 4 |  | unimplemented | RW
42802 | Fn20 | 4 |  | unimplemented | RW
42803 | CrvNam | 4 |  | unimplemented | RW
42811 | ReadOnly | 4 |  | supported | R

## 145
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
42812 | ID |  |  | 145
42813 | L |  |  | 8
42814 | Ramp Up Rate (NomRmpUpRte) |  |  | supported | RW
42815 | NomRmpDnRte |  |  | supported | RW
42816 | Emergency Ramp Up Rate (EmgRmpUpRte) |  |  | unimplemented | RW
42817 | Emergency Ramp Down Rate (EmgRmpDnRte) |  |  | unimplemented | RW
42818 | Connect Ramp Up Rate (ConnRmpUpRte) |  |  | supported | RW
42819 | Connect Ramp Down Rate (ConnRmpDnRte) |  |  | unimplemented | RW
42820 | Default Ramp Rate (AGra) |  |  | unimplemented | RW
42821 | Ramp Rate Scale Factor (Rmp_SF) |  |  | -1 | R

## 64203
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
42822 | ID |  |  | 64203
42823 | L |  |  | 12
42824 | ModEna |  |  | supported | RW
|  |  | DISABLE | supported
|  |  | ENABLE | supported
42825 | ReConn_Tms |  |  | supported | RW
42826 | ReConnMinV |  |  | supported | RW
42827 | ReConnMaxV |  |  | supported | RW
42828 | ReConnMinHz |  |  | supported | RW
42829 | ReConnMaxHz |  |  | supported | RW
42830 | VoltWattLatchTime (VWLatchTms) |  |  | supported | RW
42831 | FreqWattLatchTime (FWLatchTms) |  |  | supported | RW
42832 | Tms_SF |  |  | 0 | R
42833 | V_SF |  |  | -1 | R
42834 | Hz_SF |  |  | -2 | R
42835 | Pad |  |  |  | R