## Index
Model | Label | Description | Notes
1 | Common | Make, model and serial number information for this device
404 | String Combiner (Advanced) | An advanced string combiner including voltage and energy measurements | This model supersedes model 402
64207 | REbus Status | REbus status data that is defined commonly across Pika Energy REbus devices
64251 | Pika Energy PV Link Status | Miscellaneous PV Link status registers

## 1
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Common | 1 | uint16 |  |  | R | M | Make, model and serial number information for this device
Header |  | 1 |  | 1 | L |  | 66 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 16 | Mn | Manufacturer |  | string |  |  | R | M | Well known value registered with SunSpec for compliance
Fixed Block |  | 18 | 16 | 16 | Md | Model |  | string |  |  | R | M | Manufacturer specific value (32 chars)
Fixed Block |  | 34 | 32 | 8 | Opt | Options |  | string |  |  | R | O | Manufacturer specific value (16 chars)
Fixed Block |  | 42 | 40 | 8 | Vr | Version |  | string |  |  | R | O | Manufacturer specific value (16 chars)
Fixed Block |  | 50 | 48 | 16 | SN | Serial Number |  | string |  |  | R | M | Manufacturer specific value (32 chars)
Fixed Block |  | 66 | 64 | 1 | DA | Device Address |  | uint16 |  |  | RW | O | Modbus device address
Fixed Block |  | 67 | 65 | Size: 1; Name: Pad; Type: pad; R/W: R | O | Force even alignment

## 404
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | String Combiner (Advanced) | 404 | uint16 |  |  | R | M | An advanced string combiner including voltage and energy measurements | This model supersedes model 402
Header |  | 1 |  | 1 | L |  | 25 + (RB Count * 14) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | Size: 1; Name: DCA_SF; Type: sunssf; R/W: R | M | Current scale factor
Fixed Block |  | 3 | 1 | Size: 1; Name: DCAhr_SF; Type: sunssf; R/W: R | O | Amp-hour scale factor
Fixed Block |  | 4 | 2 | Size: 1; Name: DCV_SF; Type: sunssf; R/W: R | O | Voltage scale factor
Fixed Block |  | 5 | 3 | Size: 1; Name: DCW_SF; Type: sunssf; R/W: R | O | Power scale factor
Fixed Block |  | 6 | 4 | Size: 1; Name: DCWh_SF; Type: sunssf; R/W: R | O | Energy scale factor
Fixed Block |  | 7 | 5 | 1 | DCAMax | Rating |  | uint16 | A | DCA_SF | R | M | Maximum DC Current Rating
Fixed Block |  | 8 | 6 | 1 | N | N |  | count |  |  | R | M | Number of Inputs
Fixed Block |  | 9 | 7 | 2 | Evt | Event |  | bitfield32 |  |  | R | M | Bitmask value. Events
Fixed Block |  | 11 | 9 | 2 | EvtVnd | Vendor Event |  | bitfield32 |  |  | R | O | Bitmask value. Vendor defnied events
Fixed Block |  | 13 | 11 | 1 | DCA | Amps |  | int16 | A | DCA_SF | R | M | Total measured current
Fixed Block |  | 14 | 12 | 2 | DCAhr | Amp-hours |  | acc32 | Ah | DCAhr_SF | R | O | Total metered Amp-hours
Fixed Block |  | 16 | 14 | 1 | DCV | Voltage |  | int16 | V | DCV_SF | R | O | Output Voltage
Fixed Block |  | 17 | 15 | 1 | Tmp | Temp |  | int16 | C |  | R | O | Internal operating temperature
Fixed Block |  | 18 | 16 | 1 | DCW | Watts |  | int16 | W | DCW_SF | R | O | Output power
Fixed Block |  | 19 | 17 | 1 | DCPR | PR |  | int16 | Pct |  | R | O | DC Performance ratio value
Fixed Block |  | 20 | 18 | 2 | DCWh | Watt-hours |  | acc32 | Wh | DCWh_SF | R | O | Output energy
Fixed Block |  | 22 | 20 | Size: 1; Name: InDCA_SF; Type: sunssf; R/W: R | O | Current scale factor for inputs
Fixed Block |  | 23 | 21 | Size: 1; Name: InDCAhr_SF; Type: sunssf; R/W: R | O | Amp-hour scale factor for inputs
Fixed Block |  | 24 | 22 | Size: 1; Name: InDCV_SF; Type: sunssf; R/W: R | O | Voltage scale factor for inputs
Fixed Block |  | 25 | 23 | Size: 1; Name: InDCW_SF; Type: sunssf; R/W: R | O | Power scale factor for inputs
Fixed Block |  | 26 | 24 | Size: 1; Name: InDCWh_SF; Type: sunssf; R/W: R | O | Energy scale factor for inputs
Repeating Block |  | 27 | 0 | 1 | InID | ID |  | uint16 |  |  | R | M | Uniquely identifies this input set
Repeating Block |  | 28 | 1 | 2 | InEvt | Event |  | bitfield32 |  |  | R | M | String Input Event Flags
Repeating Block |  | 30 | 3 | 2 | InEvtVnd | Vendor Event |  | bitfield32 |  |  | R | O | String Input Vendor Event Flags
Repeating Block |  | 32 | 5 | 1 | InDCA | Amps |  | int16 | A | InDCA_SF | R | M | String Input Current
Repeating Block |  | 33 | 6 | 2 | InDCAhr | Amp-hours |  | acc32 | Ah | InDCAhr_SF | R | O | String Input Amp-Hours
Repeating Block |  | 35 | 8 | 1 | InDCV | Voltage |  | int16 | V | InDCV_SF | R | O | String Input Voltage
Repeating Block |  | 36 | 9 | 1 | InDCW | Watts |  | int16 | W | InDCW_SF | R | O | String Input Power
Repeating Block |  | 37 | 10 | 2 | InDCWh | Watt-hours |  | acc32 | Wh | InDCWh_SF | R | O | String Input Energy
Repeating Block |  | 39 | 12 | 1 | InDCPR | PR |  | uint16 | Pct |  | R | O | String Performance Ratio
Repeating Block |  | 40 | 13 | 1 | InN | N |  | uint16 |  |  | R | O | Number of modules in this input string | Configured value
bitfield32 | Evt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | Evt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | Evt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | Evt |  |  | Name: CURRENT; Value: 3
bitfield32 | Evt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | Evt |  |  | Name: POWER; Value: 5
bitfield32 | Evt |  |  | Name: PR; Value: 6
bitfield32 | Evt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | Evt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | Evt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | Evt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | Evt |  |  | Name: TEMP; Value: 11
bitfield32 | Evt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | Evt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | Evt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | Evt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | Evt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | Evt |  |  | Name: THEFT; Value: 17
bitfield32 | Evt |  |  | Name: ARC_DETECTED; Value: 18
bitfield32 | InEvt |  |  | Name: LOW_VOLTAGE; Value: 0
bitfield32 | InEvt |  |  | Name: LOW_POWER; Value: 1
bitfield32 | InEvt |  |  | Name: LOW_EFFICIENCY; Value: 2
bitfield32 | InEvt |  |  | Name: CURRENT; Value: 3
bitfield32 | InEvt |  |  | Name: VOLTAGE; Value: 4
bitfield32 | InEvt |  |  | Name: POWER; Value: 5
bitfield32 | InEvt |  |  | Name: PR; Value: 6
bitfield32 | InEvt |  |  | Name: DISCONNECTED; Value: 7
bitfield32 | InEvt |  |  | Name: FUSE_FAULT; Value: 8
bitfield32 | InEvt |  |  | Name: COMBINER_FUSE_FAULT; Value: 9
bitfield32 | InEvt |  |  | Name: COMBINER_CABINET_OPEN; Value: 10
bitfield32 | InEvt |  |  | Name: TEMP; Value: 11
bitfield32 | InEvt |  |  | Name: GROUNDFAULT; Value: 12
bitfield32 | InEvt |  |  | Name: REVERSED_POLARITY; Value: 13
bitfield32 | InEvt |  |  | Name: INCOMPATIBLE; Value: 14
bitfield32 | InEvt |  |  | Name: COMM_ERROR; Value: 15
bitfield32 | InEvt |  |  | Name: INTERNAL_ERROR; Value: 16
bitfield32 | InEvt |  |  | Name: THEFT; Value: 17
bitfield32 | InEvt |  |  | Name: ARC_DETECTED; Value: 18

## 64207
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | REbus Status | 64207 | uint16 |  |  | R | M | REbus status data that is defined commonly across Pika Energy REbus devices
Header |  | 1 |  | 1 | L |  | 12 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | P | REbus Power |  | int16 | W |  | R | M | REbus power. Positive indicates the device is sourcing to REbus, and negative indicates sinking from REbus.
Fixed Block |  | 3 | 1 | 2 | E | Accumulated Energy |  | uint32 | Wh |  | R | M | Total accumulated energy (exact definition differs by device)
Fixed Block |  | 5 | 3 | 1 | V | REbus Voltage |  | uint16 | V | VT_sf | R | M | REbus DC Bus Voltage
Fixed Block |  | 6 | 4 | 1 | I | REbus Current |  | int16 | A | I_sf | R | M | REbus current. Positive indicates the device is sourcing to REbus, and negative indicates sinking from REbus.
Fixed Block |  | 7 | 5 | 1 | T | Device Temperature |  | int16 | Deg C | VT_sf | R | M | Device temperature
Fixed Block |  | 8 | 6 | 1 | St | State |  | enum16 |  |  | R | M |  | State is a status field used by Pika Energy for operations and maintenance purposes
Fixed Block |  | 9 | 7 | 1 | Ev | Last Event |  | enum16 |  |  | R | M |  | The most recent event that occurred on the device
Fixed Block |  | 10 | 8 | 1 | RB | REbusBits |  | bitfield16 |  |  | R | M | REbus status register
Fixed Block |  | 11 | 9 | 1 | VT_sf | VT_sf |  | sunssf |  |  | R | M | Scale factor for V and T
Fixed Block |  | 12 | 10 | 1 | I_sf | I_sf |  | sunssf |  |  | R | M | Scale factor for I
Fixed Block |  | 13 | 11 | Size: 1; Name: Pad0; Type: pad; R/W: R | M
enum16 | St |  |  | Name: UNKNOWN; Label: device offline; Value: 0
enum16 | St |  |  | Name: DISABLED; Label: disabled; Value: 16
enum16 | St |  |  | Name: INITIALIZING; Label: initializing; Value: 256
enum16 | St |  |  | Name: POWERING_UP; Label: powering up; Value: 272
enum16 | St |  |  | Name: CONNECTING_BUS; Label: connecting to REbus; Value: 288
enum16 | St |  |  | Name: DISCONNECTING_BUS; Label: disconnecting REbus; Value: 304
enum16 | St |  |  | Name: TESTING_BUS; Label: testing REbus...; Value: 320
enum16 | St |  |  | Name: LOW_BUS_VOLTAGE; Label: low REbus voltage; Value: 512
enum16 | St |  |  | Name: STANDBY; Label: standby; Value: 768
enum16 | St |  |  | Name: WAITING; Label: waiting; Value: 784
enum16 | St |  |  | Name: WAITING_NO_INPUT; Label: waiting - no input; Value: 800
enum16 | St |  |  | Name: CONNECTING_GRID; Label: connecting grid; Value: 2048
enum16 | St |  |  | Name: DISCONNECTING_GRID; Label: disconnecting grid; Value: 2064
enum16 | St |  |  | Name: GRID_CONNECTED; Label: grid connected; Value: 2080
enum16 | St |  |  | Name: ISLANDED; Label: islanded; Value: 2096
enum16 | St |  |  | Name: CONNECTING_GENERATOR; Label: connecting generator; Value: 2112
enum16 | St |  |  | Name: GENERATOR_PARALLEL; Label: generator parallel; Value: 2128
enum16 | St |  |  | Name: LOW_INPUT_VOLTAGE; Label: low input voltage; Value: 4096
enum16 | St |  |  | Name: TESTING_DEVICE_INPUT; Label: testing input...; Value: 4112
enum16 | St |  |  | Name: CONNECTING_INPUT; Label: connecting input; Value: 4352
enum16 | St |  |  | Name: DISCONNECTING_INPUT; Label: disconnecting input; Value: 4368
enum16 | St |  |  | Name: CALIBRATING; Label: calibrating; Value: 4608
enum16 | St |  |  | Name: CALIBRATION_SUCCESS; Label: calibration success!; Value: 4624
enum16 | St |  |  | Name: CALIBRATION_NEEDED; Label: calibration required; Value: 4640
enum16 | St |  |  | Name: BURN_IN; Label: burning in; Value: 4656
enum16 | St |  |  | Name: BURN_IN_DONE; Label: burn in done; Value: 4672
enum16 | St |  |  | Name: SCHEDULER_OVERRIDDEN; Label: running, overridden; Value: 4864
enum16 | St |  |  | Name: SCHEDULER_DISABLED; Label: scheduler disabled; Value: 4880
enum16 | St |  |  | Name: RUNNING; Label: running; Value: 8192
enum16 | St |  |  | Name: MAKING_POWER; Label: making power; Value: 8208
enum16 | St |  |  | Name: LIMITING_POWER; Label: limiting power; Value: 6
enum16 | St |  |  | Name: LOW_WIND; Label: low wind; Value: 12288
enum16 | St |  |  | Name: HIGH_WIND; Label: high wind; Value: 12304
enum16 | St |  |  | Name: LOW_SUN; Label: low sun; Value: 12544
enum16 | St |  |  | Name: CHARGING_BATTERY; Label: charging; Value: 24576
enum16 | St |  |  | Name: FLOAT_CHARGING_BATTERY; Label: float charging; Value: 24592
enum16 | St |  |  | Name: BULK_CHARGING_BATTERY; Label: bulk charging; Value: 24608
enum16 | St |  |  | Name: ABSORPTION_CHARGING_BATTERY; Label: absorption charging; Value: 24624
enum16 | St |  |  | Name: EQUALIZE_CHARGING_BATTERY; Label: equalizing; Value: 24640
enum16 | St |  |  | Name: DISCHARGING_BATTERY; Label: discharging; Value: 24832
enum16 | St |  |  | Name: LOW_BATTERY_VOLTAGE; Label: low battery voltage; Value: 24848
enum16 | St |  |  | Name: ERROR_GENERIC; Label: error; Value: 28672
enum16 | St |  |  | Name: OVER_VOLTAGE_INPUT; Label: over voltage input; Value: 28688
enum16 | St |  |  | Name: OVER_VOLTAGE_OUTPUT; Label: over voltage output; Value: 28704
enum16 | St |  |  | Name: OVER_CURRENT_INPUT; Label: over current input; Value: 28720
enum16 | St |  |  | Name: OVER_CURRENT_OUTPUT; Label: over current output; Value: 28736
enum16 | St |  |  | Name: ERROR_LOW_BATTERY_VOLTAGE; Label: error: low batt volts; Value: 28752
enum16 | St |  |  | Name: OVER_TEMPERATURE; Label: over temp shutdown; Value: 41216
enum16 | St |  |  | Name: GROUND_FAULT; Label: ground fault; Value: 49152
enum16 | St |  |  | Name: INSULATION_FAULT; Label: err: insulation fault; Value: 29200
enum16 | St |  |  | Name: CALIBRATION_0; Label: calibration mode; Value: 32256
enum16 | St |  |  | Name: CALIBRATION_1; Label: calibration 1; Value: 32272
enum16 | St |  |  | Name: CALIBRATION_2; Label: calibration 2; Value: 32288
enum16 | St |  |  | Name: CALIBRATION_3; Label: calibration 3; Value: 32304
enum16 | Ev |  |  | Name: GENERIC; Label: unknown event; Value: 32768
enum16 | Ev |  |  | Name: POWERUP; Label: power up; Value: 32784
enum16 | Ev |  |  | Name: SUPPLY_UNDERVOLTAGE; Label: supply under voltage; Value: 32800
enum16 | Ev |  |  | Name: DAILY_EVENT; Label: daily event; Value: 32816
enum16 | Ev |  |  | Name: ENABLE; Label: enable; Value: 33024
enum16 | Ev |  |  | Name: DISABLE; Label: disable; Value: 33280
enum16 | Ev |  |  | Name: MANUAL_DISABLE; Label: manual disable; Value: 33296
enum16 | Ev |  |  | Name: EXTERNAL_ESTOP; Label: external estop; Value: 33312
enum16 | Ev |  |  | Name: SYSMODE_CHANGE; Label: sysmode change; Value: 33536
enum16 | Ev |  |  | Name: SYSMODE_BAD; Label: unauthorized sysmode; Value: 33792
enum16 | Ev |  |  | Name: DEBUG_TRACE; Label: debug trace recorded; Value: 34048
enum16 | Ev |  |  | Name: TOU_ENTRY_ACTIVATED; Label: TOU entry activated; Value: 34304
enum16 | Ev |  |  | Name: SOFTWARE_VERSION; Label: software version; Value: 36832
enum16 | Ev |  |  | Name: HARDWARE_VERSION; Label: hardware version mismatch; Value: 36848
enum16 | Ev |  |  | Name: INTERRUPT_FAULT; Label: interrupt fault; Value: 36864
enum16 | Ev |  |  | Name: GATEDRIVE_FAULT; Label: gate drive fault; Value: 37120
enum16 | Ev |  |  | Name: TIMER_FAULT; Label: timer fault; Value: 37376
enum16 | Ev |  |  | Name: TRANSISTOR_FAILURE; Label: transistor failure; Value: 39168
enum16 | Ev |  |  | Name: OVER_TEMPERATURE; Label: over temp shutdown; Value: 41216
enum16 | Ev |  |  | Name: FAN_FAILURE; Label: fan failure; Value: 41232
enum16 | Ev |  |  | Name: FUSE_BLOWN; Label: fuse blown; Value: 41248
enum16 | Ev |  |  | Name: MISWIRING; Label: miswiring fault; Value: 41472
enum16 | Ev |  |  | Name: ALTERNATOR_BAD; Label: alternator bad; Value: 42496
enum16 | Ev |  |  | Name: REVERSE_ROTATION; Label: reverse rotation; Value: 42752
enum16 | Ev |  |  | Name: BUS_FAULT; Label: REbus fault; Value: 45056
enum16 | Ev |  |  | Name: BUS_NO_LOAD; Label: REbus no load; Value: 45072
enum16 | Ev |  |  | Name: BUS_OVER_VOLTAGE; Label: REbus over voltage; Value: 45312
enum16 | Ev |  |  | Name: BUS_UNDER_VOLTAGE; Label: REbus under voltage; Value: 45328
enum16 | Ev |  |  | Name: BUS_OVER_CURRENT; Label: REbus over current; Value: 45568
enum16 | Ev |  |  | Name: INTERNAL_OVERVOLTAGE; Label: internal over voltage; Value: 45824
enum16 | Ev |  |  | Name: BATTERY_GENERIC; Label: battery generic; Value: 47104
enum16 | Ev |  |  | Name: BATTERY_READY; Label: battery ready; Value: 47120
enum16 | Ev |  |  | Name: BATTERY_NOT_READY; Label: battery not ready; Value: 47136
enum16 | Ev |  |  | Name: BMS_GENERIC; Label: BMS generic; Value: 47360
enum16 | Ev |  |  | Name: BMS_ALARM; Label: BMS alarm; Value: 47376
enum16 | Ev |  |  | Name: BMS_WARNING; Label: BMS warning; Value: 47392
enum16 | Ev |  |  | Name: BMS_ERROR; Label: BMS error; Value: 47408
enum16 | Ev |  |  | Name: GROUND_FAULT; Label: ground fault; Value: 49152
enum16 | Ev |  |  | Name: INPUT_LOW; Label: input low; Value: 49408
enum16 | Ev |  |  | Name: INPUT_SENSOR_FAULT; Label: input sensor fault; Value: 49664
enum16 | Ev |  |  | Name: INPUT_OVER_CURRENT; Label: input over current; Value: 49920
enum16 | Ev |  |  | Name: INPUT_OVERSPEED; Label: input overspeed; Value: 50176
enum16 | Ev |  |  | Name: INPUT_HIGH; Label: input high; Value: 50432
enum16 | Ev |  |  | Name: ARC_FAULT; Label: arc fault; Value: 50688
enum16 | Ev |  |  | Name: INPUT_READY; Label: input ready; Value: 50944
enum16 | Ev |  |  | Name: GRID_FAULT; Label: grid fault; Value: 53248
enum16 | Ev |  |  | Name: GRID_OVER_VOLTAGE; Label: grid over voltage; Value: 53264
enum16 | Ev |  |  | Name: GRID_OVER_CURRENT; Label: grid over current; Value: 53280
enum16 | Ev |  |  | Name: GRID_OVER_FREQUENCY; Label: grid over frequency; Value: 53296
enum16 | Ev |  |  | Name: GRID_UNDER_VOLTAGE; Label: grid under voltage; Value: 53312
enum16 | Ev |  |  | Name: GRID_UNDER_FREQUENCY; Label: grid under frequency; Value: 53328
enum16 | Ev |  |  | Name: GRID_OVER_VOLTAGE_FAST; Label: grid overvoltage fast; Value: 53344
enum16 | Ev |  |  | Name: GRID_HIGH_IMPEDANCE; Label: grid high impedance; Value: 53360
enum16 | Ev |  |  | Name: TRANSFER_FAIL; Label: transfer sw fail; Value: 53504
enum16 | Ev |  |  | Name: SETPOINT_CRC_FAULT; Label: setpoint crc fault; Value: 57344
enum16 | Ev |  |  | Name: EEPROM_FAULT; Label: EEPROM failure; Value: 57600
enum16 | Ev |  |  | Name: FLASH_FAULT; Label: FLASH fault; Value: 57856
enum16 | Ev |  |  | Name: PLM_RESTART; Label: PLM restart; Value: 58112
enum16 | Ev |  |  | Name: DEFAULT_TRAP; Label: default trap; Value: 61440
enum16 | Ev |  |  | Name: ADDRESS_ERROR; Label: address error trap; Value: 61456
enum16 | Ev |  |  | Name: STACK_ERROR; Label: stack error trap; Value: 61472
enum16 | Ev |  |  | Name: OSCILLATOR_FAIL; Label: osc. fail trap; Value: 61488
enum16 | Ev |  |  | Name: MATH_ERROR; Label: math error trap; Value: 61504
enum16 | Ev |  |  | Name: DMAC_ERROR; Label: dmac error trap; Value: 61520
bitfield16 | RB |  |  | Name: ENABLE_MASTER; Value: 0
bitfield16 | RB |  |  | Name: ENABLE_SOURCE; Value: 1
bitfield16 | RB |  |  | Name: ENABLE_SINK; Value: 2
bitfield16 | RB |  |  | Name: REBUS_CONNECTED; Value: 3
bitfield16 | RB |  |  | Name: SOURCING; Value: 4
bitfield16 | RB |  |  | Name: SINKING; Value: 5
bitfield16 | RB |  |  | Name: LIMITING_POWER; Label: limiting power; Value: 6
bitfield16 | RB |  |  | Name: TEMP_LIMIT; Value: 7
bitfield16 | RB |  |  | Name: BUS_VOLTAGE_LOW; Value: 8
bitfield16 | RB |  |  | Name: DEV_VOLTAGE_LOW; Value: 9
bitfield16 | RB |  |  | Name: BUS_VOLTAGE_HIGH; Value: 10
bitfield16 | RB |  |  | Name: DEV_VOLTAGE_HIGH; Value: 11
bitfield16 | RB |  |  | Name: TEMPERATURE_HIGH; Value: 12
bitfield16 | RB |  |  | Name: SPT_INVALID; Value: 13
bitfield16 | RB |  |  | Name: GROUNDFAULT; Value: 14
bitfield16 | RB |  |  | Name: SUPPLY_VOLTAGE_LOW; Value: 15

## 64251
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Pika Energy PV Link Status | 64251 | uint16 |  |  | R | M | Miscellaneous PV Link status registers
Header |  | 1 |  | 1 | L |  | 22 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ErrorWord | Error status |  | bitfield16 |  |  | R | M | Error status bitfield
Fixed Block |  | 3 | 1 | 1 | EnableBits | Enable bits |  | bitfield16 |  |  | R | M | Internal status register
Fixed Block |  | 4 | 2 | 1 | StatusWord | General status |  | bitfield16 |  |  | R | M | General system status
Fixed Block |  | 5 | 3 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 6 | 4 | Size: 1; Name: I_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 7 | 5 | 1 | Vin | PV String Voltage |  | int16 |  | V_SF | R | M | Input voltage of PV string
Fixed Block |  | 8 | 6 | 1 | Iin | PV String Current |  | int16 |  | I_SF | R | M | Input current of PV string
Fixed Block |  | 9 | 7 | 1 | AMax | Maximum Input Current |  | int16 |  | I_SF | RW | M | Maximum permitted input current from PV string
Fixed Block |  | 10 | 8 | 1 | Ena | Enable or Disable PV Link |  | enum16 |  |  | RW | M
Fixed Block |  | 11 | 9 | 1 | Pad0 | Pad |  | pad |  |  | R | M | Large pad for future model expansion
Fixed Block |  | 12 | 10 | Size: 1; Name: Pad1; Type: pad; R/W: R | M
Fixed Block |  | 13 | 11 | Size: 1; Name: Pad2; Type: pad; R/W: R | M
Fixed Block |  | 14 | 12 | Size: 1; Name: Pad3; Type: pad; R/W: R | M
Fixed Block |  | 15 | 13 | Size: 1; Name: Pad4; Type: pad; R/W: R | M
Fixed Block |  | 16 | 14 | Size: 1; Name: Pad5; Type: pad; R/W: R | M
Fixed Block |  | 17 | 15 | Size: 1; Name: Pad6; Type: pad; R/W: R | M
Fixed Block |  | 18 | 16 | Size: 1; Name: Pad7; Type: pad; R/W: R | M
Fixed Block |  | 19 | 17 | Size: 1; Name: Pad8; Type: pad; R/W: R | M
Fixed Block |  | 20 | 18 | Size: 1; Name: Pad9; Type: pad; R/W: R | M
Fixed Block |  | 21 | 19 | Size: 1; Name: Pad10; Type: pad; R/W: R | M
Fixed Block |  | 22 | 20 | Size: 1; Name: Pad11; Type: pad; R/W: R | M
Fixed Block |  | 23 | 21 | Size: 1; Name: Pad12; Type: pad; R/W: R | M
bitfield16 | ErrorWord |  |  | Name: UNUSED0; Value: 0
bitfield16 | ErrorWord |  |  | Name: HW_ARC_FAULT; Value: 1
bitfield16 | ErrorWord |  |  | Name: HW_REVERSE_CURRENT; Value: 2
bitfield16 | ErrorWord |  |  | Name: OVER_CURRENT; Value: 3
bitfield16 | ErrorWord |  |  | Name: INPUT_OVERVOLTAGE; Value: 4
bitfield16 | ErrorWord |  |  | Name: GFTEST_FAIL; Value: 5
bitfield16 | ErrorWord |  |  | Name: LOW_INPUT_IMPEDANCE; Value: 6
bitfield16 | ErrorWord |  |  | Name: UNUSED7; Value: 7
bitfield16 | ErrorWord |  |  | Name: UNUSED8; Value: 8
bitfield16 | ErrorWord |  |  | Name: FLASH_FAILURE; Value: 9
bitfield16 | ErrorWord |  |  | Name: EEPROM_FAILURE; Value: 10
bitfield16 | ErrorWord |  |  | Name: SPT_CRC_FAIL; Value: 11
bitfield16 | ErrorWord |  |  | Name: OVER_TEMP; Value: 12
bitfield16 | ErrorWord |  |  | Name: UNUSED13; Value: 13
bitfield16 | ErrorWord |  |  | Name: DEAD_FET; Value: 14
bitfield16 | ErrorWord |  |  | Name: HWV_MISMATCH; Value: 15
bitfield16 | EnableBits |  |  | Name: DEADMAN; Value: 0
bitfield16 | EnableBits |  |  | Name: UNUSED1; Value: 1
bitfield16 | EnableBits |  |  | Name: UNUSED2; Value: 2
bitfield16 | EnableBits |  |  | Name: UNUSED3; Value: 3
bitfield16 | EnableBits |  |  | Name: CONNECT_INPUT; Value: 4
bitfield16 | EnableBits |  |  | Name: CONNECT_OUTPUT; Value: 5
bitfield16 | EnableBits |  |  | Name: UNUSED6; Value: 6
bitfield16 | EnableBits |  |  | Name: UNUSED7; Value: 7
bitfield16 | EnableBits |  |  | Name: UNUSED8; Value: 8
bitfield16 | EnableBits |  |  | Name: GF_STARTTEST; Value: 9
bitfield16 | EnableBits |  |  | Name: INPUT_IMPED_STARTTEST; Value: 11
bitfield16 | EnableBits |  |  | Name: UNUSED11; Value: 11
bitfield16 | EnableBits |  |  | Name: PHASE2; Value: 12
bitfield16 | EnableBits |  |  | Name: UNUSED13; Value: 13
bitfield16 | EnableBits |  |  | Name: UNUSED14; Value: 14
bitfield16 | EnableBits |  |  | Name: UNUSED15; Value: 15
bitfield16 | StatusWord |  |  | Name: DEADMAN_UP; Value: 0
bitfield16 | StatusWord |  |  | Name: LOW_SUPPLY_VOLTAGE; Value: 1
bitfield16 | StatusWord |  |  | Name: GF_TESTED; Value: 2
bitfield16 | StatusWord |  |  | Name: INPUT_IMPED_TESTED; Value: 3
bitfield16 | StatusWord |  |  | Name: INPUT_CONNECTED; Value: 4
bitfield16 | StatusWord |  |  | Name: OUTPUT_CONNECTED; Value: 5
bitfield16 | StatusWord |  |  | Name: INPUT_DISCONNETED; Value: 6
bitfield16 | StatusWord |  |  | Name: OUTPUT_DISCONNETED; Value: 7
bitfield16 | StatusWord |  |  | Name: GF_SW_ACTIVE; Value: 8
bitfield16 | StatusWord |  |  | Name: MASTER_FAULT_ACTIVE; Value: 9
bitfield16 | StatusWord |  |  | Name: GF_ACTIVE; Value: 10
bitfield16 | StatusWord |  |  | Name: ARC_FAULT_ACTIVE; Value: 11
bitfield16 | StatusWord |  |  | Name: PBUS_LOW; Value: 12
bitfield16 | StatusWord |  |  | Name: UNBAL_INPUT_FAULT_ACTIVE; Value: 13
bitfield16 | StatusWord |  |  | Name: PH2_ON; Value: 14
bitfield16 | StatusWord |  |  | Name: PH2_OFF; Value: 15
enum16 | Ena |  |  | Name: DISABLE; Value: 0
enum16 | Ena |  |  | Name: ENABLE; Value: 1