## Info
Date | 2018-06-27 11:26:09
Manufacturer Name | Pika Energy
Product Name | Harbor Smart Battery
Product Models | B301
Product Description

## 1
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40002 | ID |  |  | 1
40003 | L |  |  | 66
40004 | Manufacturer (Mn) |  |  | Pika | R
40020 | Model (Md) |  |  | Smart Battery | R
40036 | Options (Opt) |  |  | unimplemented | R
40044 | Version (Vr) |  |  | 1214_12420 | R
40052 | Serial Number (SN) |  |  | 000100080119 | R
40068 | Device Address (DA) |  |  | unimplemented | RW
40069 | Pad |  |  |  | R

## 64207
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40070 | ID |  |  | 64207
40071 | L |  |  | 12
40072 | REbus Power (P) |  |  | supported | R
40073 | Accumulated Energy (E) |  |  | supported | R
40075 | REbus Voltage (V) |  |  | supported | R
40076 | REbus Current (I) |  |  | supported | R
40077 | Device Temperature (T) |  |  | supported | R
40078 | State (St) |  |  | supported | R
|  |  | device offline (UNKNOWN) | supported
|  |  | disabled (DISABLED) | supported
|  |  | initializing (INITIALIZING) | supported
|  |  | powering up (POWERING_UP) | supported
|  |  | connecting to REbus (CONNECTING_BUS) | supported
|  |  | disconnecting REbus (DISCONNECTING_BUS) | supported
|  |  | testing REbus... (TESTING_BUS) | supported
|  |  | low REbus voltage (LOW_BUS_VOLTAGE) | supported
|  |  | standby (STANDBY) | supported
|  |  | waiting (WAITING) | supported
|  |  | waiting - no input (WAITING_NO_INPUT) | supported
|  |  | connecting grid (CONNECTING_GRID) | supported
|  |  | disconnecting grid (DISCONNECTING_GRID) | supported
|  |  | grid connected (GRID_CONNECTED) | supported
|  |  | islanded (ISLANDED) | supported
|  |  | connecting generator (CONNECTING_GENERATOR) | supported
|  |  | generator parallel (GENERATOR_PARALLEL) | supported
|  |  | low input voltage (LOW_INPUT_VOLTAGE) | supported
|  |  | testing input... (TESTING_DEVICE_INPUT) | supported
|  |  | connecting input (CONNECTING_INPUT) | supported
|  |  | disconnecting input (DISCONNECTING_INPUT) | supported
|  |  | calibrating (CALIBRATING) | supported
|  |  | calibration success! (CALIBRATION_SUCCESS) | supported
|  |  | calibration required (CALIBRATION_NEEDED) | supported
|  |  | burning in (BURN_IN) | supported
|  |  | burn in done (BURN_IN_DONE) | supported
|  |  | running, overridden (SCHEDULER_OVERRIDDEN) | supported
|  |  | scheduler disabled (SCHEDULER_DISABLED) | supported
|  |  | running (RUNNING) | supported
|  |  | making power (MAKING_POWER) | supported
|  |  | limiting power (LIMITING_POWER) | supported
|  |  | low wind (LOW_WIND) | supported
|  |  | high wind (HIGH_WIND) | supported
|  |  | low sun (LOW_SUN) | supported
|  |  | charging (CHARGING_BATTERY) | supported
|  |  | float charging (FLOAT_CHARGING_BATTERY) | supported
|  |  | bulk charging (BULK_CHARGING_BATTERY) | supported
|  |  | absorption charging (ABSORPTION_CHARGING_BATTERY) | supported
|  |  | equalizing (EQUALIZE_CHARGING_BATTERY) | supported
|  |  | discharging (DISCHARGING_BATTERY) | supported
|  |  | low battery voltage (LOW_BATTERY_VOLTAGE) | supported
|  |  | error (ERROR_GENERIC) | supported
|  |  | over voltage input (OVER_VOLTAGE_INPUT) | supported
|  |  | over voltage output (OVER_VOLTAGE_OUTPUT) | supported
|  |  | over current input (OVER_CURRENT_INPUT) | supported
|  |  | over current output (OVER_CURRENT_OUTPUT) | supported
|  |  | error: low batt volts (ERROR_LOW_BATTERY_VOLTAGE) | supported
|  |  | over temp shutdown (OVER_TEMPERATURE) | supported
|  |  | ground fault (GROUND_FAULT) | supported
|  |  | err: insulation fault (INSULATION_FAULT) | supported
|  |  | calibration mode (CALIBRATION_0) | supported
|  |  | calibration 1 (CALIBRATION_1) | supported
|  |  | calibration 2 (CALIBRATION_2) | supported
|  |  | calibration 3 (CALIBRATION_3) | supported
40079 | Last Event (Ev) |  |  | supported | R
|  |  | unknown event (GENERIC) | supported
|  |  | power up (POWERUP) | supported
|  |  | supply under voltage (SUPPLY_UNDERVOLTAGE) | supported
|  |  | daily event (DAILY_EVENT) | supported
|  |  | enable (ENABLE) | supported
|  |  | disable (DISABLE) | supported
|  |  | manual disable (MANUAL_DISABLE) | supported
|  |  | external estop (EXTERNAL_ESTOP) | supported
|  |  | sysmode change (SYSMODE_CHANGE) | supported
|  |  | unauthorized sysmode (SYSMODE_BAD) | supported
|  |  | debug trace recorded (DEBUG_TRACE) | supported
|  |  | TOU entry activated (TOU_ENTRY_ACTIVATED) | supported
|  |  | software version (SOFTWARE_VERSION) | supported
|  |  | hardware version mismatch (HARDWARE_VERSION) | supported
|  |  | interrupt fault (INTERRUPT_FAULT) | supported
|  |  | gate drive fault (GATEDRIVE_FAULT) | supported
|  |  | timer fault (TIMER_FAULT) | supported
|  |  | transistor failure (TRANSISTOR_FAILURE) | supported
|  |  | over temp shutdown (OVER_TEMPERATURE) | supported
|  |  | fan failure (FAN_FAILURE) | supported
|  |  | fuse blown (FUSE_BLOWN) | supported
|  |  | miswiring fault (MISWIRING) | supported
|  |  | alternator bad (ALTERNATOR_BAD) | supported
|  |  | reverse rotation (REVERSE_ROTATION) | supported
|  |  | REbus fault (BUS_FAULT) | supported
|  |  | REbus no load (BUS_NO_LOAD) | supported
|  |  | REbus over voltage (BUS_OVER_VOLTAGE) | supported
|  |  | REbus under voltage (BUS_UNDER_VOLTAGE) | supported
|  |  | REbus over current (BUS_OVER_CURRENT) | supported
|  |  | internal over voltage (INTERNAL_OVERVOLTAGE) | supported
|  |  | battery generic (BATTERY_GENERIC) | supported
|  |  | battery ready (BATTERY_READY) | supported
|  |  | battery not ready (BATTERY_NOT_READY) | supported
|  |  | BMS generic (BMS_GENERIC) | supported
|  |  | BMS alarm (BMS_ALARM) | supported
|  |  | BMS warning (BMS_WARNING) | supported
|  |  | BMS error (BMS_ERROR) | supported
|  |  | ground fault (GROUND_FAULT) | supported
|  |  | input low (INPUT_LOW) | supported
|  |  | input sensor fault (INPUT_SENSOR_FAULT) | supported
|  |  | input over current (INPUT_OVER_CURRENT) | supported
|  |  | input overspeed (INPUT_OVERSPEED) | supported
|  |  | input high (INPUT_HIGH) | supported
|  |  | arc fault (ARC_FAULT) | supported
|  |  | input ready (INPUT_READY) | supported
|  |  | grid fault (GRID_FAULT) | supported
|  |  | grid over voltage (GRID_OVER_VOLTAGE) | supported
|  |  | grid over current (GRID_OVER_CURRENT) | supported
|  |  | grid over frequency (GRID_OVER_FREQUENCY) | supported
|  |  | grid under voltage (GRID_UNDER_VOLTAGE) | supported
|  |  | grid under frequency (GRID_UNDER_FREQUENCY) | supported
|  |  | grid overvoltage fast (GRID_OVER_VOLTAGE_FAST) | supported
|  |  | grid high impedance (GRID_HIGH_IMPEDANCE) | supported
|  |  | transfer sw fail (TRANSFER_FAIL) | supported
|  |  | setpoint crc fault (SETPOINT_CRC_FAULT) | supported
|  |  | EEPROM failure (EEPROM_FAULT) | supported
|  |  | FLASH fault (FLASH_FAULT) | supported
|  |  | PLM restart (PLM_RESTART) | supported
|  |  | default trap (DEFAULT_TRAP) | supported
|  |  | address error trap (ADDRESS_ERROR) | supported
|  |  | stack error trap (STACK_ERROR) | supported
|  |  | osc. fail trap (OSCILLATOR_FAIL) | supported
|  |  | math error trap (MATH_ERROR) | supported
|  |  | dmac error trap (DMAC_ERROR) | supported
40080 | REbusBits (RB) |  |  | supported | R
|  |  | ENABLE_MASTER | supported
|  |  | ENABLE_SOURCE | supported
|  |  | ENABLE_SINK | supported
|  |  | REBUS_CONNECTED | supported
|  |  | SOURCING | supported
|  |  | SINKING | supported
|  |  | limiting power (LIMITING_POWER) | supported
|  |  | TEMP_LIMIT | supported
|  |  | BUS_VOLTAGE_LOW | supported
|  |  | DEV_VOLTAGE_LOW | supported
|  |  | BUS_VOLTAGE_HIGH | supported
|  |  | DEV_VOLTAGE_HIGH | supported
|  |  | TEMPERATURE_HIGH | supported
|  |  | SPT_INVALID | supported
|  |  | GROUNDFAULT | supported
|  |  | SUPPLY_VOLTAGE_LOW | supported
40081 | VT_sf |  |  | -1 | R
40082 | I_sf |  |  | -2 | R
40083 | Pad0 |  |  |  | R

## 64209
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40084 | ID |  |  | 64209
40085 | L |  |  | 22
40086 | Total Energy In (WhIn) |  |  | supported | R
40088 | Total Energy Out (WhOut) |  |  | supported | R
40090 | Error status (ErrorWord) |  |  | supported | R
|  |  | CS_ZERO_ERR | supported
|  |  | REF_FAIL | supported
|  |  | THERM_FAIL | supported
|  |  | UNUSED | supported
|  |  | EEPROM_FAIL | supported
|  |  | SPT_ERROR | supported
|  |  | HWV_MISMATCH | supported
|  |  | SPTV_MISMATCH | supported
|  |  | BATT_OVERTEMP | supported
|  |  | REPEAT_OVERCURRENT | supported
|  |  | FAN_FAIL | supported
|  |  | CURRENT_CTRL_FAIL | supported
|  |  | BMS_ERROR | supported
|  |  | REPEAT_CONTACT | supported
|  |  | EXTERNAL_STOP | supported
|  |  | GROUND_FAULT | supported
40091 | Enable bits (EnableBits) |  |  | supported | R
|  |  | DEADMAN | supported
|  |  | GATEDRIVE | supported
|  |  | REBUS_CONNECT | supported
|  |  | BATT_CONNECT | supported
|  |  | INT_FAN | supported
|  |  | EXT_FAN | supported
|  |  | FAN_OVERRIDE | supported
|  |  | BLKSTART_BATT_CHG | supported
|  |  | CONV1 | supported
|  |  | CONV2 | supported
|  |  | AUTOMODE | supported
|  |  | 120HZ_FILTER | supported
|  |  | BMS | supported
|  |  | INHIBIT_CSZ | supported
|  |  | CSZERO | supported
|  |  | USB_RCP | supported
40092 | InhibitBits |  |  | supported | R
|  |  | PRECHARGE_FAIL | supported
|  |  | IBAT_INTEGRAL | supported
|  |  | NO_REBUS_ENABLES | supported
|  |  | BATTERY_BMS | supported
|  |  | VBUS_OV | supported
|  |  | VDC_OV | supported
|  |  | VBAT_OV | supported
|  |  | IBAT_OV | supported
|  |  | NO_INPUT | supported
|  |  | BATT_VERYLOW_TIMEOUT | supported
|  |  | BATT_CRIT_LOW | supported
|  |  | BATT_CRIT_HIGH | supported
|  |  | UNUSED12 | supported
|  |  | UNUSED13 | supported
|  |  | UNUSED14 | supported
|  |  | UNUSED15 | supported
40093 | General Status (StatusBits) |  |  | supported | R
|  |  | DEADMAN_UP | supported
|  |  | REBUS_PRECHARGING | supported
|  |  | REBUS_CONNECTED | supported
|  |  | BATT_CONNECTED | supported
|  |  | CHARGING | supported
|  |  | DISCHARGING | supported
|  |  | COULD_CHARGE | supported
|  |  | COULD_DISCHARGE | supported
|  |  | UNUSED8 | supported
|  |  | UNUSED9 | supported
|  |  | UNUSED10 | supported
|  |  | UNUSED11 | supported
|  |  | GFD_READY | supported
|  |  | PLM_READY | supported
|  |  | UNUSED14 | supported
|  |  | UNUSED15 | supported
40094 | BMS Status (BMSStatus) |  |  | supported | R
|  |  | ENABLE_DISCHARGE | supported
|  |  | LOW_SOC | supported
|  |  | VERYLOW_SOC | supported
|  |  | CRITLOW_SOC | supported
|  |  | ENABLE_CHARGE | supported
|  |  | HIGH_SOC | supported
|  |  | VERYHIGH_SOC | supported
|  |  | CRITHIGH_SOC | supported
|  |  | BMS_UP | supported
|  |  | COMM_OK | supported
|  |  | BATT_READY | supported
|  |  | UNUSED | supported
|  |  | CHARGE_WARNING | supported
|  |  | DISCHARGE_WARNING | supported
|  |  | UNUSED14 | supported
|  |  | FLOAT | supported
40095 | Pad (Pad0) |  |  |  | R
40096 | Pad1 |  |  |  | R
40097 | Pad2 |  |  |  | R
40098 | Pad3 |  |  |  | R
40099 | Pad4 |  |  |  | R
40100 | Pad5 |  |  |  | R
40101 | Pad6 |  |  |  | R
40102 | Pad7 |  |  |  | R
40103 | Pad8 |  |  |  | R
40104 | Pad9 |  |  |  | R
40105 | Pad10 |  |  |  | R
40106 | Pad11 |  |  |  | R
40107 | Pad12 |  |  |  | R

## 802
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40108 | ID |  |  | 802
40109 | L |  |  | 62
40110 | Nameplate Charge Capacity (AHRtg) |  |  | supported | R
40111 | Nameplate Energy Capacity (WHRtg) |  |  | supported | R
40112 | Nameplate Max Charge Rate (WChaRteMax) |  |  | supported | R
40113 | Namplate Max Discharge Rate (WDisChaRteMax) |  |  | supported | R
40114 | Self Discharge Rate (DisChaRte) |  |  | unimplemented | R
40115 | Nameplate Max SoC (SoCMax) |  |  | supported | RW
40116 | Nameplate Min SoC (SoCMin) |  |  | supported | RW
40117 | Max Reserve Percent (SocRsvMax) |  |  | supported | RW
40118 | Min Reserve Percent (SoCRsvMin) |  |  | supported | RW
40119 | State of Charge (SoC) |  |  | supported | R
40120 | Depth of Discharge (DoD) |  |  | unimplemented | R
40121 | State of Health (SoH) |  |  | supported | R
40122 | Cycle Count (NCyc) |  |  | unimplemented | R
40124 | Charge Status (ChaSt) |  |  | unimplemented | R
|  |  | OFF | supported
|  |  | EMPTY | supported
|  |  | DISCHARGING | supported
|  |  | CHARGING | supported
|  |  | FULL | supported
|  |  | HOLDING | supported
|  |  | TESTING | supported
40125 | Control Mode (LocRemCtl) |  |  | unimplemented | R
|  |  | Remote Control (REMOTE) | supported
|  |  | Local Control (LOCAL) | supported
40126 | Battery Heartbeat (Hb) |  |  | unimplemented | R
40127 | Controller Heartbeat (CtrlHb) |  |  | unimplemented | RW
40128 | Alarm Reset (AlmRst) |  |  | unimplemented | RW
40129 | Battery Type (Typ) |  |  | supported | R
|  |  | Not Applicable or Unknown (NOT APPLICABLE_UNKNOWN) | supported
|  |  | Lead-Acid (LEAD_ACID) | supported
|  |  | Nickel-Metal Hydrate (NICKEL_METAL_HYDRATE) | supported
|  |  | Nickel-Cadmium (NICKEL_CADMIUM) | supported
|  |  | Lithium-Ion (LITHIUM_ION) | supported
|  |  | Carbon-Zinc (CARBON_ZINC) | supported
|  |  | Zinc Chloride (ZINC_CHLORIDE) | supported
|  |  | Alkaline (ALKALINE) | supported
|  |  | Rechargeable Alkaline (RECHARGEABLE_ALKALINE) | supported
|  |  | Sodium-Sulfur (SODIUM_SULFUR) | supported
|  |  | Flow (FLOW) | supported
|  |  | Other (OTHER) | supported
40130 | State of the Battery Bank (State) |  |  | supported | R
|  |  | Disconnected (DISCONNECTED) | supported
|  |  | Initializing (INITIALIZING) | supported
|  |  | Connected (CONNECTED) | supported
|  |  | Standby (STANDBY) | supported
|  |  | SoC Protection (SOC PROTECTION) | supported
|  |  | Fault (FAULT) | supported
40131 | Pad (Pad1) |  |  |  | R
40132 | Warranty Date (WarrDt) |  |  | unimplemented | R
40134 | Battery Event 1 Bitfield (Evt1) |  |  | supported | R
|  |  | Communication Error (COMMUNICATION_ERROR) | supported
|  |  | Over Temperature Alarm (OVER_TEMP_ALARM) | supported
|  |  | Over Temperature Warning (OVER_TEMP_WARNING) | supported
|  |  | Under Temperature Alarm (UNDER_TEMP_ALARM) | supported
|  |  | Under Temperature Warning (UNDER_TEMP_WARNING) | supported
|  |  | Over Charge Current Alarm (OVER_CHARGE_CURRENT_ALARM) | supported
|  |  | Over Charge Current Warning (OVER_CHARGE_CURRENT_WARNING) | supported
|  |  | Over Discharge Current Alarm (OVER_DISCHARGE_CURRENT_ALARM) | supported
|  |  | Over Discharge Current Warning (OVER_DISCHARGE_CURRENT_WARNING) | supported
|  |  | Over Voltage Alarm (OVER_VOLT_ALARM) | supported
|  |  | Over Voltage Warning (OVER_VOLT_WARNING) | supported
|  |  | Under Voltage Alarm (UNDER_VOLT_ALARM) | supported
|  |  | Under Voltage Warning (UNDER_VOLT_WARNING) | supported
|  |  | Under State of Charge Min Alarm (UNDER_SOC_MIN_ALARM) | supported
|  |  | Under State of Charge Min Warning (UNDER_SOC_MIN_WARNING) | supported
|  |  | Over State of Charge Max Alarm (OVER_SOC_MAX_ALARM) | supported
|  |  | Over State of Charge Max Warning (OVER_SOC_MAX_WARNING) | supported
|  |  | Voltage Imbalance Warning (VOLTAGE_IMBALANCE_WARNING) | supported
|  |  | Temperature Imbalance Alarm (TEMPERATURE_IMBALANCE_ALARM) | supported
|  |  | Temperature Imbalance Warning (TEMPERATURE_IMBALANCE_WARNING) | supported
|  |  | Contactor Error (CONTACTOR_ERROR) | supported
|  |  | Fan Error (FAN_ERROR) | supported
|  |  | Ground Fault Error (GROUND_FAULT) | supported
|  |  | Open Door Error (OPEN_DOOR_ERROR) | supported
|  |  | Current Imbalance Warning (CURRENT_IMBALANCE_WARNING) | supported
|  |  | Other Battery Alarm (OTHER_ALARM) | supported
|  |  | Other Battery Warning (OTHER_WARNING) | supported
40136 | Battery Event 2 Bitfield (Evt2) |  |  | supported | R
40138 | Vendor Event Bitfield 1 (EvtVnd1) |  |  | supported | R
40140 | Vendor Event Bitfield 2 (EvtVnd2) |  |  | supported | R
40142 | External Battery Voltage (V) |  |  | supported | R
40143 | Max Battery Voltage (VMax) |  |  | unimplemented | R
40144 | Min Battery Voltage (VMin) |  |  | unimplemented | R
40145 | Max Cell Voltage (CellVMax) |  |  | supported | R
40146 | Max Cell Voltage String (CellVMaxStr) |  |  | unimplemented | R
40147 | Max Cell Voltage Module (CellVMaxMod) |  |  | unimplemented | R
40148 | Min Cell Voltage (CellVMin) |  |  | supported | R
40149 | Min Cell Voltage String (CellVMinStr) |  |  | unimplemented | R
40150 | Min Cell Voltage Module (CellVMinMod) |  |  | unimplemented | R
40151 | Average Cell Voltage (CellVAvg) |  |  | unimplemented | R
40152 | Total DC Current (A) |  |  | supported | R
40153 | Max Charge Current (AChaMax) |  |  | supported | RW
40154 | Max Discharge Current (ADisChaMax) |  |  | supported | RW
40155 | Total Power (W) |  |  | supported | R
40156 | Inverter State Request (ReqInvState) |  |  | unimplemented | R
|  |  | No Request (NO REQUEST) | supported
|  |  | Start Inverter (START) | supported
|  |  | Stop Inverter (STOP) | supported
40157 | Battery Power Request (ReqW) |  |  | unimplemented | R
40158 | Set Operation (SetOp) |  |  | unimplemented | RW
|  |  | Connect the Battery Bank (CONNECT) | supported
|  |  | Disconnect the Battery Bank (DISCONNECT) | supported
40159 | Set Inverter State (SetInvState) |  |  | unimplemented | RW
|  |  | Inverter is Stopped (INVERTER_STOPPED) | supported
|  |  | Inverter is in Standby (INVERTER_STANDBY) | supported
|  |  | Inverter is Started (INVERTER_STARTED) | supported
40160 | AHRtg_SF |  |  | -2 | R
40161 | WHRtg_SF |  |  | 0 | R
40162 | WChaDisChaMax_SF |  |  | 0 | R
40163 | DisChaRte_SF |  |  | 0 | R
40164 | SoC_SF |  |  | -1 | R
40165 | DoD_SF |  |  | 0 | R
40166 | SoH_SF |  |  | -1 | R
40167 | V_SF |  |  | -1 | R
40168 | CellV_SF |  |  | -3 | R
40169 | A_SF |  |  | -2 | R
40170 | AMax_SF |  |  | -2 | R
40171 | W_SF |  |  | 0 | R

## 804
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40172 | ID |  |  | 804
40173 | L |  |  | 110
40174 | String Index (Idx) |  |  | unimplemented | R
40175 | Module Count (NMod) |  |  | supported | R
40176 | String Status (St) |  |  | unimplemented | R
|  |  | String Is Enabled (STRING_ENABLED) | supported
|  |  | Contactor Status (CONTACTOR_STATUS) | supported
40178 | Connection Failure Reason (ConFail) |  |  | unimplemented | R
|  |  | No Failure (NO_FAILURE) | supported
|  |  | Button Pushed (BUTTON_PUSHED) | supported
|  |  | Ground Fault (STR_GROUND_FAULT) | supported
|  |  | Outside Voltage Range (OUTSIDE_VOLTAGE_RANGE) | supported
|  |  | String Not Enabled (STRING_NOT_ENABLED) | supported
|  |  | Fuse Open (FUSE_OPEN) | supported
|  |  | Contactor Failure (CONTACTOR_FAILURE) | supported
|  |  | Precharge Failure (PRECHARGE_FAILURE) | supported
|  |  | String Fault (STRING_FAULT) | supported
40179 | String Cell Balancing Count (NCellBal) |  |  | unimplemented | R
40180 | String State of Charge (SoC) |  |  | supported | R
40181 | String Depth of Discharge (DoD) |  |  | unimplemented | R
40182 | String Cycle Count (NCyc) |  |  | unimplemented | R
40184 | String State of Health (SoH) |  |  | supported | R
40185 | String Current (A) |  |  | supported | R
40186 | String Voltage (V) |  |  | supported | R
40187 | Max Cell Voltage (CellVMax) |  |  | supported | R
40188 | Max Cell Voltage Module (CellVMaxMod) |  |  | unimplemented | R
40189 | Min Cell Voltage (CellVMin) |  |  | supported | R
40190 | Min Cell Voltage Module (CellVMinMod) |  |  | unimplemented | R
40191 | Average Cell Voltage (CellVAvg) |  |  | unimplemented | R
40192 | Max Module Temperature (ModTmpMax) |  |  | supported | R
40193 | Max Module Temperature Module (ModTmpMaxMod) |  |  | unimplemented | R
40194 | Min Module Temperature (ModTmpMin) |  |  | supported | R
40195 | Min Module Temperature Module (ModTmpMinMod) |  |  | unimplemented | R
40196 | Average Module Temperature (ModTmpAvg) |  |  | supported | R
40197 | Pad (Pad1) |  |  |  | R
40198 | Contactor Status (ConSt) |  |  | unimplemented | R
|  |  | Contactor 0 Closed (CONTACTOR_0) | supported
|  |  | Contactor 1 Closed (CONTACTOR_1) | supported
|  |  | Contactor 2 Closed (CONTACTOR_2) | supported
|  |  | Contactor 3 Closed (CONTACTOR_3) | supported
|  |  | Contactor 4 Closed (CONTACTOR_4) | supported
|  |  | Contactor 5 Closed (CONTACTOR_5) | supported
|  |  | Contactor 6 Closed (CONTACTOR_6) | supported
|  |  | Contactor 7 Closed (CONTACTOR_7) | supported
|  |  | Contactor 8 Closed (CONTACTOR_8) | supported
|  |  | Contactor 9 Closed (CONTACTOR_9) | supported
|  |  | Contactor 10 Closed (CONTACTOR_10) | supported
|  |  | Contactor 11 Closed (CONTACTOR_11) | supported
|  |  | Contactor 12 Closed (CONTACTOR_12) | supported
|  |  | Contactor 13 Closed (CONTACTOR_13) | supported
|  |  | Contactor 14 Closed (CONTACTOR_14) | supported
|  |  | Contactor 15 Closed (CONTACTOR_15) | supported
|  |  | Contactor 16 Closed (CONTACTOR_16) | supported
|  |  | Contactor 17 Closed (CONTACTOR_17) | supported
|  |  | Contactor 18 Closed (CONTACTOR_18) | supported
|  |  | Contactor 19 Closed (CONTACTOR_19) | supported
|  |  | Contactor 20 Closed (CONTACTOR_20) | supported
|  |  | Contactor 21 Closed (CONTACTOR_21) | supported
|  |  | Contactor 22 Closed (CONTACTOR_22) | supported
|  |  | Contactor 23 Closed (CONTACTOR_23) | supported
|  |  | Contactor 24 Closed (CONTACTOR_24) | supported
|  |  | Contactor 25 Closed (CONTACTOR_25) | supported
|  |  | Contactor 26 Closed (CONTACTOR_26) | supported
|  |  | Contactor 27 Closed (CONTACTOR_27) | supported
|  |  | Contactor 28 Closed (CONTACTOR_28) | supported
|  |  | Contactor 29 Closed (CONTACTOR_29) | supported
|  |  | Contactor 30 Closed (CONTACTOR_30) | supported
40200 | String Event 1 (Evt1) |  |  | unimplemented | R
|  |  | Communication Error (COMMUNICATION_ERROR) | supported
|  |  | Over Temperature Alarm (OVER_TEMP_ALARM) | supported
|  |  | Over Temperature Warning (OVER_TEMP_WARNING) | supported
|  |  | Under Temperature Alarm (UNDER_TEMP_ALARM) | supported
|  |  | Under Temperature Warning (UNDER_TEMP_WARNING) | supported
|  |  | Over Charge Current Alarm (OVER_CHARGE_CURRENT_ALARM) | supported
|  |  | Over Charge Current Warning (OVER_CHARGE_CURRENT_WARNING) | supported
|  |  | Over Discharge Current Alarm (OVER_DISCHARGE_CURRENT_ALARM) | supported
|  |  | Over Discharge Current Warning (OVER_DISCHARGE_CURRENT_WARNING) | supported
|  |  | Over Voltage Alarm (OVER_VOLT_ALARM) | supported
|  |  | Over Voltage Warning (OVER_VOLT_WARNING) | supported
|  |  | Under Voltage Alarm (UNDER_VOLT_ALARM) | supported
|  |  | Under Voltage Warning (UNDER_VOLT_WARNING) | supported
|  |  | Under State of Charge Min Alarm (UNDER_SOC_MIN_ALARM) | supported
|  |  | Under State of Charge Min Warning (UNDER_SOC_MIN_WARNING) | supported
|  |  | Over State of Charge Max Alarm (OVER_SOC_MAX_ALARM) | supported
|  |  | Over State of Charge Max Warning (OVER_SOC_MAX_WARNING) | supported
|  |  | Voltage Imbalance Warning (VOLTAGE_IMBALANCE_WARNING) | supported
|  |  | Temperature Imbalance Alarm (TEMPERATURE_IMBALANCE_ALARM) | supported
|  |  | Temperature Imbalance Warning (TEMPERATURE_IMBALANCE_WARNING) | supported
|  |  | Contactor Error (CONTACTOR_ERROR) | supported
|  |  | Fan Error (FAN_ERROR) | supported
|  |  | Ground Fault Error (GROUND_FAULT) | supported
|  |  | Open Door Error (OPEN_DOOR_ERROR) | supported
|  |  | Reserved (RESERVED_1) | supported
|  |  | Other String Alarm (OTHER_ALARM) | supported
|  |  | Other String Warning (OTHER_WARNING) | supported
|  |  | Reserved (RESERVED_2) | supported
|  |  | Configuation Alarm (CONFIGURATION_ALARM) | supported
|  |  | Configuation Warning (CONFIGURATION_WARNING) | supported
40202 | String Event 2 (Evt2) |  |  | unimplemented | R
40204 | Vendor Event Bitfield 1 (EvtVnd1) |  |  | unimplemented | R
40206 | Vendor Event Bitfield 2 (EvtVnd2) |  |  | unimplemented | R
40208 | Enable/Disable String (SetEna) |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40209 | Connect/Disconnect String (SetCon) |  |  | unimplemented | RW
|  |  | Connect String (CONNECT_STRING) | supported
|  |  | Disconnect String (DISCONNECT_STRING) | supported
40210 | SoC_SF |  |  | -1 | R
40211 | SoH_SF |  |  | -1 | R
40212 | DoD_SF |  |  | -1 | R
40213 | A_SF |  |  | -2 | R
40214 | V_SF |  |  | -1 | R
40215 | CellV_SF |  |  | -3 | R
40216 | ModTmp_SF |  |  | -1 | R
40217 | Pad (Pad2) |  |  |  | R
40218 | Pad (Pad3) |  |  |  | R
40219 | Pad (Pad4) |  |  |  | R
40220 | Module Cell Count (ModNCell) | 1 |  | supported | R
40221 | Module SoC (ModSoC) | 1 |  | supported | R
40222 | Module SoH (ModSoH) | 1 |  | supported | R
40223 | Max Cell Voltage (ModCellVMax) | 1 |  | supported | R
40224 | Max Cell Voltage Cell (ModCellVMaxCell) | 1 |  | unimplemented | R
40225 | Min Cell Voltage (ModCellVMin) | 1 |  | supported | R
40226 | Min Cell Voltage Cell (ModCellVMinCell) | 1 |  | unimplemented | R
40227 | Average Cell Voltage (ModCellVAvg) | 1 |  | supported | R
40228 | Max Cell Temperature (ModCellTmpMax) | 1 |  | supported | R
40229 | Max Cell Temperature Cell (ModCellTmpMaxCell) | 1 |  | unimplemented | R
40230 | Min Cell Temperature (ModCellTmpMin) | 1 |  | supported | R
40231 | Min Cell Temperature Cell (ModCellTmpMinCell) | 1 |  | unimplemented | R
40232 | Average Cell Temperature (ModCellTmpAvg) | 1 |  | supported | R
40233 | Pad (Pad5) | 1 |  |  | R
40234 | Pad (Pad6) | 1 |  |  | R
40235 | Pad (Pad7) | 1 |  |  | R
40236 | Module Cell Count (ModNCell) | 2 |  | supported | R
40237 | Module SoC (ModSoC) | 2 |  | supported | R
40238 | Module SoH (ModSoH) | 2 |  | supported | R
40239 | Max Cell Voltage (ModCellVMax) | 2 |  | supported | R
40240 | Max Cell Voltage Cell (ModCellVMaxCell) | 2 |  | unimplemented | R
40241 | Min Cell Voltage (ModCellVMin) | 2 |  | supported | R
40242 | Min Cell Voltage Cell (ModCellVMinCell) | 2 |  | unimplemented | R
40243 | Average Cell Voltage (ModCellVAvg) | 2 |  | supported | R
40244 | Max Cell Temperature (ModCellTmpMax) | 2 |  | supported | R
40245 | Max Cell Temperature Cell (ModCellTmpMaxCell) | 2 |  | unimplemented | R
40246 | Min Cell Temperature (ModCellTmpMin) | 2 |  | supported | R
40247 | Min Cell Temperature Cell (ModCellTmpMinCell) | 2 |  | unimplemented | R
40248 | Average Cell Temperature (ModCellTmpAvg) | 2 |  | supported | R
40249 | Pad (Pad5) | 2 |  |  | R
40250 | Pad (Pad6) | 2 |  |  | R
40251 | Pad (Pad7) | 2 |  |  | R
40252 | Module Cell Count (ModNCell) | 3 |  | supported | R
40253 | Module SoC (ModSoC) | 3 |  | supported | R
40254 | Module SoH (ModSoH) | 3 |  | supported | R
40255 | Max Cell Voltage (ModCellVMax) | 3 |  | supported | R
40256 | Max Cell Voltage Cell (ModCellVMaxCell) | 3 |  | unimplemented | R
40257 | Min Cell Voltage (ModCellVMin) | 3 |  | supported | R
40258 | Min Cell Voltage Cell (ModCellVMinCell) | 3 |  | unimplemented | R
40259 | Average Cell Voltage (ModCellVAvg) | 3 |  | supported | R
40260 | Max Cell Temperature (ModCellTmpMax) | 3 |  | supported | R
40261 | Max Cell Temperature Cell (ModCellTmpMaxCell) | 3 |  | unimplemented | R
40262 | Min Cell Temperature (ModCellTmpMin) | 3 |  | supported | R
40263 | Min Cell Temperature Cell (ModCellTmpMinCell) | 3 |  | unimplemented | R
40264 | Average Cell Temperature (ModCellTmpAvg) | 3 |  | supported | R
40265 | Pad (Pad5) | 3 |  |  | R
40266 | Pad (Pad6) | 3 |  |  | R
40267 | Pad (Pad7) | 3 |  |  | R
40268 | Module Cell Count (ModNCell) | 4 |  | supported | R
40269 | Module SoC (ModSoC) | 4 |  | supported | R
40270 | Module SoH (ModSoH) | 4 |  | supported | R
40271 | Max Cell Voltage (ModCellVMax) | 4 |  | supported | R
40272 | Max Cell Voltage Cell (ModCellVMaxCell) | 4 |  | unimplemented | R
40273 | Min Cell Voltage (ModCellVMin) | 4 |  | supported | R
40274 | Min Cell Voltage Cell (ModCellVMinCell) | 4 |  | unimplemented | R
40275 | Average Cell Voltage (ModCellVAvg) | 4 |  | supported | R
40276 | Max Cell Temperature (ModCellTmpMax) | 4 |  | supported | R
40277 | Max Cell Temperature Cell (ModCellTmpMaxCell) | 4 |  | unimplemented | R
40278 | Min Cell Temperature (ModCellTmpMin) | 4 |  | supported | R
40279 | Min Cell Temperature Cell (ModCellTmpMinCell) | 4 |  | unimplemented | R
40280 | Average Cell Temperature (ModCellTmpAvg) | 4 |  | supported | R
40281 | Pad (Pad5) | 4 |  |  | R
40282 | Pad (Pad6) | 4 |  |  | R
40283 | Pad (Pad7) | 4 |  |  | R

## 64252
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40284 | ID |  |  | 64252
40285 | L |  |  | 80
40286 | sf_10 |  |  | -1 | R
40287 | sf_100 |  |  | -2 | R
40288 | sf_1000 |  |  | -3 | R
40289 | Module Count (NMod) |  |  | supported | R
40290 | WhIn |  |  | supported | R
40292 | WhOut |  |  | supported | R
40294 | AhIn |  |  | supported | R
40296 | AhOut |  |  | supported | R
40298 | Heat Sink Temp (THSin) |  |  | supported | R
40299 | Power (W) |  |  | supported | R
40300 | Current (I) |  |  | supported | R
40301 | String Voltage (V) |  |  | supported | R
40302 | Serial Number (SN) | 1 |  | supported | R
40303 | Product Date Code (ManDt) | 1 |  | supported | R
40304 | Program Version (ProgVer) | 1 |  | supported | R
40305 | Data Version (DataVer) | 1 |  | supported | R
40306 | Status Flags (StatusFlags) | 1 |  | supported | R
40307 | Warning Flags (WarningFlags) | 1 |  | supported | R
40308 | Alarm Flags (AlarmFlags) | 1 |  | supported | R
40309 | Error Flags (ErrorFlags) | 1 |  | supported | R
40310 | Module IO Flags (ModuleIOFlags) | 1 |  | supported | R
40311 | State of Charge (SOC) | 1 |  | supported | R
40312 | State of Health (SOH) | 1 |  | supported | R
40313 | MaxCellV | 1 |  | supported | R
40314 | MinCellV | 1 |  | supported | R
40315 | PackV | 1 |  | supported | R
40316 | MaxCellT | 1 |  | supported | R
40317 | MinCellT | 1 |  | supported | R
40318 | Serial Number (SN) | 2 |  | supported | R
40319 | Product Date Code (ManDt) | 2 |  | supported | R
40320 | Program Version (ProgVer) | 2 |  | supported | R
40321 | Data Version (DataVer) | 2 |  | supported | R
40322 | Status Flags (StatusFlags) | 2 |  | supported | R
40323 | Warning Flags (WarningFlags) | 2 |  | supported | R
40324 | Alarm Flags (AlarmFlags) | 2 |  | supported | R
40325 | Error Flags (ErrorFlags) | 2 |  | supported | R
40326 | Module IO Flags (ModuleIOFlags) | 2 |  | supported | R
40327 | State of Charge (SOC) | 2 |  | supported | R
40328 | State of Health (SOH) | 2 |  | supported | R
40329 | MaxCellV | 2 |  | supported | R
40330 | MinCellV | 2 |  | supported | R
40331 | PackV | 2 |  | supported | R
40332 | MaxCellT | 2 |  | supported | R
40333 | MinCellT | 2 |  | supported | R
40334 | Serial Number (SN) | 3 |  | supported | R
40335 | Product Date Code (ManDt) | 3 |  | supported | R
40336 | Program Version (ProgVer) | 3 |  | supported | R
40337 | Data Version (DataVer) | 3 |  | supported | R
40338 | Status Flags (StatusFlags) | 3 |  | supported | R
40339 | Warning Flags (WarningFlags) | 3 |  | supported | R
40340 | Alarm Flags (AlarmFlags) | 3 |  | supported | R
40341 | Error Flags (ErrorFlags) | 3 |  | supported | R
40342 | Module IO Flags (ModuleIOFlags) | 3 |  | supported | R
40343 | State of Charge (SOC) | 3 |  | supported | R
40344 | State of Health (SOH) | 3 |  | supported | R
40345 | MaxCellV | 3 |  | supported | R
40346 | MinCellV | 3 |  | supported | R
40347 | PackV | 3 |  | supported | R
40348 | MaxCellT | 3 |  | supported | R
40349 | MinCellT | 3 |  | supported | R
40350 | Serial Number (SN) | 4 |  | supported | R
40351 | Product Date Code (ManDt) | 4 |  | supported | R
40352 | Program Version (ProgVer) | 4 |  | supported | R
40353 | Data Version (DataVer) | 4 |  | supported | R
40354 | Status Flags (StatusFlags) | 4 |  | supported | R
40355 | Warning Flags (WarningFlags) | 4 |  | supported | R
40356 | Alarm Flags (AlarmFlags) | 4 |  | supported | R
40357 | Error Flags (ErrorFlags) | 4 |  | supported | R
40358 | Module IO Flags (ModuleIOFlags) | 4 |  | supported | R
40359 | State of Charge (SOC) | 4 |  | supported | R
40360 | State of Health (SOH) | 4 |  | supported | R
40361 | MaxCellV | 4 |  | supported | R
40362 | MinCellV | 4 |  | supported | R
40363 | PackV | 4 |  | supported | R
40364 | MaxCellT | 4 |  | supported | R
40365 | MinCellT | 4 |  | supported | R