## Index
Model | Label | Description | Notes
1 | Common | Make, model and serial number information for this device
802 | Battery Base Model
804 | Lithium-Ion String Model
64207 | REbus Status | REbus status data that is defined commonly across Pika Energy REbus devices
64209 | Pika Energy B-Link Status | Miscellaneous battery status registers
64252 | Panasonic DCB105 Module Warranty Data | Data from DCB105 modules required for Panasonic warranty

## 1
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Common | 1 | uint16 |  |  | R | M | Make, model and serial number information for this device
Header |  | 1 |  | 1 | L |  | 66 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 16 | Mn | Manufacturer |  | string |  |  | R | M | Well known value registered with SunSpec for compliance
Fixed Block |  | 18 | 16 | 16 | Md | Model |  | string |  |  | R | M | Manufacturer specific value (32 chars)
Fixed Block |  | 34 | 32 | 8 | Opt | Options |  | string |  |  | R | O | Manufacturer specific value (16 chars)
Fixed Block |  | 42 | 40 | 8 | Vr | Version |  | string |  |  | R | O | Manufacturer specific value (16 chars)
Fixed Block |  | 50 | 48 | 16 | SN | Serial Number |  | string |  |  | R | M | Manufacturer specific value (32 chars)
Fixed Block |  | 66 | 64 | 1 | DA | Device Address |  | uint16 |  |  | RW | O | Modbus device address
Fixed Block |  | 67 | 65 | Size: 1; Name: Pad; Type: pad; R/W: R | O | Force even alignment

## 802
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Battery Base Model | 802 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 62 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | AHRtg | Nameplate Charge Capacity |  | uint16 | Ah | AHRtg_SF | R | M | Nameplate charge capacity in amp-hours.
Fixed Block |  | 3 | 1 | 1 | WHRtg | Nameplate Energy Capacity |  | uint16 | Wh | WHRtg_SF | R | M | Nameplate energy capacity in DC watt-hours.
Fixed Block |  | 4 | 2 | 1 | WChaRteMax | Nameplate Max Charge Rate |  | uint16 | W | WChaDisChaMax_SF | R | M | Maximum rate of energy transfer into the storage device in DC watts.
Fixed Block |  | 5 | 3 | 1 | WDisChaRteMax | Namplate Max Discharge Rate |  | uint16 | W | WChaDisChaMax_SF | R | M | Maximum rate of energy transfer out of the storage device in DC watts.
Fixed Block |  | 6 | 4 | 1 | DisChaRte | Self Discharge Rate |  | uint16 | %WHRtg | DisChaRte_SF | R | O | Self discharge rate. Percentage of capacity (WHRtg) discharged per day.
Fixed Block |  | 7 | 5 | 1 | SoCMax | Nameplate Max SoC |  | uint16 | %WHRtg | SoC_SF | RW | O | Manufacturer maximum state of charge, expressed as a percentage.
Fixed Block |  | 8 | 6 | 1 | SoCMin | Nameplate Min SoC |  | uint16 | %WHRtg | SoC_SF | RW | O | Manufacturer minimum state of charge, expressed as a percentage.
Fixed Block |  | 9 | 7 | 1 | SocRsvMax | Max Reserve Percent |  | uint16 | %WHRtg | SoC_SF | RW | O | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage.
Fixed Block |  | 10 | 8 | 1 | SoCRsvMin | Min Reserve Percent |  | uint16 | %WHRtg | SoC_SF | RW | O | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage.
Fixed Block |  | 11 | 9 | 1 | SoC | State of Charge |  | uint16 | %WHRtg | SoC_SF | R | M | State of charge, expressed as a percentage. | Measurement.
Fixed Block |  | 12 | 10 | 1 | DoD | Depth of Discharge |  | uint16 | % | DoD_SF | R | O | Depth of discharge, expressed as a percentage. | Measurement.
Fixed Block |  | 13 | 11 | 1 | SoH | State of Health |  | uint16 | % | SoH_SF | R | O | Percentage of battery life remaining.
Fixed Block |  | 14 | 12 | 2 | NCyc | Cycle Count |  | uint32 |  |  | R | O | Number of cycles executed in the battery.
Fixed Block |  | 16 | 14 | 1 | ChaSt | Charge Status |  | enum16 |  |  | R | O | Charge status of storage device. Enumeration.
Fixed Block |  | 17 | 15 | 1 | LocRemCtl | Control Mode |  | enum16 |  |  | R | M | Battery control mode. Enumeration. | Maps to DRCC.LocRemCtl in IEC 61850.
Fixed Block |  | 18 | 16 | 1 | Hb | Battery Heartbeat |  | uint16 |  |  | R | O | Value is incremented every second with periodic resets to zero.
Fixed Block |  | 19 | 17 | 1 | CtrlHb | Controller Heartbeat |  | uint16 |  |  | RW | O | Value is incremented every second with periodic resets to zero.
Fixed Block |  | 20 | 18 | 1 | AlmRst | Alarm Reset |  | uint16 |  |  | RW | M | Used to reset any latched alarms. 1 = Reset. | Battery should reset to 0 when reset is complete.
Fixed Block |  | 21 | 19 | 1 | Typ | Battery Type |  | enum16 |  |  | R | M | Type of battery. Enumeration. | Maps to DBAT.BatTyp in 61850.
Fixed Block |  | 22 | 20 | 1 | State | State of the Battery Bank |  | enum16 |  |  | R | M | State of the battery bank. Enumeration. | Must be reconciled with State in IEC 61850.
Fixed Block |  | 23 | 21 | 1 | Pad1 | Pad |  | pad |  |  | R | M | Pad register.
Fixed Block |  | 24 | 22 | 2 | WarrDt | Warranty Date |  | uint32 |  |  | R | O | Date the device warranty expires. | Number of days since 1/1/2000.
Fixed Block |  | 26 | 24 | 2 | Evt1 | Battery Event 1 Bitfield |  | bitfield32 |  |  | R | M | Alarms and warnings. Bit flags.
Fixed Block |  | 28 | 26 | 2 | Evt2 | Battery Event 2 Bitfield |  | bitfield32 |  |  | R | M | Alarms and warnings. Bit flags. | Reserved for future use.
Fixed Block |  | 30 | 28 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | M | Vendor defined events.
Fixed Block |  | 32 | 30 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | M | Vendor defined events.
Fixed Block |  | 34 | 32 | 1 | V | External Battery Voltage |  | uint16 | V | V_SF | R | M | DC Bus Voltage. | Maps to ZBAT.V in IEC 61850.
Fixed Block |  | 35 | 33 | 1 | VMax | Max Battery Voltage |  | uint16 | V | V_SF | R | O | Instantaneous maximum battery voltage. | If not implemented, must implement AChaMax and ADisChaMax.
Fixed Block |  | 36 | 34 | 1 | VMin | Min Battery Voltage |  | uint16 | V | V_SF | R | O | Instantaneous minimum battery voltage. | If not implemented, must implement AChaMax and ADisChaMax.
Fixed Block |  | 37 | 35 | 1 | CellVMax | Max Cell Voltage |  | uint16 | V | CellV_SF | R | O | Maximum voltage for all cells in the bank. | Measurement.
Fixed Block |  | 38 | 36 | 1 | CellVMaxStr | Max Cell Voltage String |  | uint16 |  |  | R | O | String containing the cell with maximum voltage.
Fixed Block |  | 39 | 37 | 1 | CellVMaxMod | Max Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with maximum voltage.
Fixed Block |  | 40 | 38 | 1 | CellVMin | Min Cell Voltage |  | uint16 | V | CellV_SF | R | O | Minimum voltage for all cells in the bank. | Measurement.
Fixed Block |  | 41 | 39 | 1 | CellVMinStr | Min Cell Voltage String |  | uint16 |  |  | R | O | String containing the cell with minimum voltage.
Fixed Block |  | 42 | 40 | 1 | CellVMinMod | Min Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with minimum voltage.
Fixed Block |  | 43 | 41 | 1 | CellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | O | Average cell voltage for all cells in the bank. | Calculation based on measurements.
Fixed Block |  | 44 | 42 | 1 | A | Total DC Current |  | int16 | A | A_SF | R | M | Total DC current flowing to/from the battery bank. | Measurement.
Fixed Block |  | 45 | 43 | 1 | AChaMax | Max Charge Current |  | uint16 | A | AMax_SF | RW | O | Instantaneous maximum DC charge current. | Setpoint. Changed to R/W by Pika.
Fixed Block |  | 46 | 44 | 1 | ADisChaMax | Max Discharge Current |  | uint16 | A | AMax_SF | RW | O | Instantaneous maximum DC discharge current. | Setpoint. Changed to R/W by Pika.
Fixed Block |  | 47 | 45 | 1 | W | Total Power |  | int16 | W | W_SF | R | M | Total power flowing to/from the battery bank. | Measurement.
Fixed Block |  | 48 | 46 | 1 | ReqInvState | Inverter State Request |  | enum16 |  |  | R | O | Request from battery to start or stop the inverter. Enumeration. | Used in special states such as manual battery charging.
Fixed Block |  | 49 | 47 | 1 | ReqW | Battery Power Request |  | int16 | W | W_SF | R | O | AC Power requested by battery. | Used in special states such as string balancing.
Fixed Block |  | 50 | 48 | 1 | SetOp | Set Operation |  | enum16 |  |  | RW | M | Instruct the battery bank to perform an operation such as connecting. Enumeration.
Fixed Block |  | 51 | 49 | 1 | SetInvState | Set Inverter State |  | enum16 |  |  | RW | M | Set the current state of the inverter. | Information needed by battery for some operations.
Fixed Block |  | 52 | 50 | Size: 1; Name: AHRtg_SF; Type: sunssf; R/W: R | M | Scale factor for charge capacity.
Fixed Block |  | 53 | 51 | Size: 1; Name: WHRtg_SF; Type: sunssf; R/W: R | M | Scale factor for energy capacity.
Fixed Block |  | 54 | 52 | Size: 1; Name: WChaDisChaMax_SF; Type: sunssf; R/W: R | M | Scale factor for maximum charge and discharge rate.
Fixed Block |  | 55 | 53 | Size: 1; Name: DisChaRte_SF; Type: sunssf; R/W: R | O | Scale factor for self discharge rate.
Fixed Block |  | 56 | 54 | Size: 1; Name: SoC_SF; Type: sunssf; R/W: R | M | Scale factor for state of charge values.
Fixed Block |  | 57 | 55 | Size: 1; Name: DoD_SF; Type: sunssf; R/W: R | O | Scale factor for depth of discharge.
Fixed Block |  | 58 | 56 | Size: 1; Name: SoH_SF; Type: sunssf; R/W: R | O | Scale factor for state of health.
Fixed Block |  | 59 | 57 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M | Scale factor for DC bus voltage.
Fixed Block |  | 60 | 58 | Size: 1; Name: CellV_SF; Type: sunssf; R/W: R | M | Scale factor for cell voltage.
Fixed Block |  | 61 | 59 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Scale factor for DC current.
Fixed Block |  | 62 | 60 | Size: 1; Name: AMax_SF; Type: sunssf; R/W: R | M | Scale factor for instantationous DC charge/discharge current.
Fixed Block |  | 63 | 61 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | O | Scale factor for AC power request.
enum16 | ChaSt |  |  | Name: OFF; Value: 1
enum16 | ChaSt |  |  | Name: EMPTY; Value: 2
enum16 | ChaSt |  |  | Name: DISCHARGING; Value: 3
enum16 | ChaSt |  |  | Name: CHARGING; Value: 4
enum16 | ChaSt |  |  | Name: FULL; Value: 5
enum16 | ChaSt |  |  | Name: HOLDING; Value: 6
enum16 | ChaSt |  |  | Name: TESTING; Value: 7
enum16 | LocRemCtl |  |  | Name: REMOTE; Label: Remote Control; Value: 0 |  | Battery is controlled remotely (e.g. by the site controller). | Value of 0 matches LocRemCtl in IEC 61850.
enum16 | LocRemCtl |  |  | Name: LOCAL; Label: Local Control; Value: 1 |  | Battery is controlled by a local operator (e.g. through battery HMI). | Value of 1 matches LocRemCtl in IEC 61850.
enum16 | Typ |  |  | Name: NOT APPLICABLE_UNKNOWN; Label: Not Applicable or Unknown; Value: 0 |  | Battery type is not applicable or unknown.
enum16 | Typ |  |  | Name: LEAD_ACID; Label: Lead-Acid; Value: 1 |  | Lead-acid battery type.
enum16 | Typ |  |  | Name: NICKEL_METAL_HYDRATE; Label: Nickel-Metal Hydrate; Value: 2 |  | Nickel-metal hydrate battery type.
enum16 | Typ |  |  | Name: NICKEL_CADMIUM; Label: Nickel-Cadmium; Value: 3 |  | Nickel-cadmium battery type.
enum16 | Typ |  |  | Name: LITHIUM_ION; Label: Lithium-Ion; Value: 4 |  | Lithium-ion battery type.
enum16 | Typ |  |  | Name: CARBON_ZINC; Label: Carbon-Zinc; Value: 5 |  | Carbon-zinc battery type.
enum16 | Typ |  |  | Name: ZINC_CHLORIDE; Label: Zinc Chloride; Value: 6 |  | Zinc chloride battery type.
enum16 | Typ |  |  | Name: ALKALINE; Label: Alkaline; Value: 7 |  | Alkaline battery type.
enum16 | Typ |  |  | Name: RECHARGEABLE_ALKALINE; Label: Rechargeable Alkaline; Value: 8 |  | Rechargeable alkaline battery type.
enum16 | Typ |  |  | Name: SODIUM_SULFUR; Label: Sodium-Sulfur; Value: 9 |  | Sodium-sulfur battery type.
enum16 | Typ |  |  | Name: FLOW; Label: Flow; Value: 10 |  | Flow battery type.
enum16 | Typ |  |  | Name: OTHER; Label: Other; Value: 99 |  | Other battery type.
enum16 | State |  |  | Name: DISCONNECTED; Label: Disconnected; Value: 1 |  | Battery bank is disconnected. All contactors are open.
enum16 | State |  |  | Name: INITIALIZING; Label: Initializing; Value: 2 |  | Battery bank is initializing but not ready for operating. String balancing may occur.
enum16 | State |  |  | Name: CONNECTED; Label: Connected; Value: 3 |  | Battery bank is ready for operation. All enabled contactors are closed.
enum16 | State |  |  | Name: STANDBY; Label: Standby; Value: 4 |  | Battery bank is connected and in standby/power saving mode.
enum16 | State |  |  | Name: SOC PROTECTION; Label: SoC Protection; Value: 5 |  | Battery bank is connected but SoC is too low. Battery should be considered "offline".
enum16 | State |  |  | Name: FAULT; Label: Fault; Value: 99 |  | The battery has experienced a critical failure and may not be operated.
bitfield32 | Evt1 |  |  | Name: COMMUNICATION_ERROR; Label: Communication Error; Value: 0 |  | Unable to communcate with BMS or BMS is unable to communicate with battery strings.
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_ALARM; Label: Over Temperature Alarm; Value: 1 |  | Battery has exceeded maximum operating temperature
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_WARNING; Label: Over Temperature Warning; Value: 2 |  | Battery is approaching maximum operating temperature.
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_ALARM; Label: Under Temperature Alarm; Value: 3 |  | Battery has exceeded minimum operating temperature
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_WARNING; Label: Under Temperature Warning; Value: 4 |  | Battery is approaching minimum operating temperature.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_ALARM; Label: Over Charge Current Alarm; Value: 5 |  | Battery maximum charge current has been exceeded. | See AChaMax.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_WARNING; Label: Over Charge Current Warning; Value: 6 |  | Approaching battery maximum charge current. | See AChaMax.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_ALARM; Label: Over Discharge Current Alarm; Value: 7 |  | Battery maximum discharge current has been exceeded. | See ADisChaMax.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_WARNING; Label: Over Discharge Current Warning; Value: 8 |  | Approaching battery maximum discharge current. | See ADisChaMax.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_ALARM; Label: Over Voltage Alarm; Value: 9 |  | Battery voltage has exceeded maximum limit.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_WARNING; Label: Over Voltage Warning; Value: 10 |  | Battery voltage is approaching maximum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_ALARM; Label: Under Voltage Alarm; Value: 11 |  | Battery voltage has exceeded minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_WARNING; Label: Under Voltage Warning; Value: 12 |  | Battery voltage is approaching minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_ALARM; Label: Under State of Charge Min Alarm; Value: 13 |  | Battery state of charge has reached or exceeded SoCMin
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_WARNING; Label: Under State of Charge Min Warning; Value: 14 |  | Battery state of charge is approaching SoCMin
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_ALARM; Label: Over State of Charge Max Alarm; Value: 15 |  | Battery state of charge has reached or exceeded SoCMax
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_WARNING; Label: Over State of Charge Max Warning; Value: 16 |  | Battery state of charge is approaching SoCMax
bitfield32 | Evt1 |  |  | Name: VOLTAGE_IMBALANCE_WARNING; Label: Voltage Imbalance Warning; Value: 17 |  | A voltage imbalance exists between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: TEMPERATURE_IMBALANCE_ALARM; Label: Temperature Imbalance Alarm; Value: 18 |  | A temperature imbalance exists between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: TEMPERATURE_IMBALANCE_WARNING; Label: Temperature Imbalance Warning; Value: 19 |  | A temperature imbalance is developing between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: CONTACTOR_ERROR; Label: Contactor Error; Value: 20 |  | A contactor failed to open or close as requested.
bitfield32 | Evt1 |  |  | Name: FAN_ERROR; Label: Fan Error; Value: 21 |  | One or more battery fans has failed.
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground Fault Error; Value: 22 |  | Ground fault detected.
bitfield32 | Evt1 |  |  | Name: OPEN_DOOR_ERROR; Label: Open Door Error; Value: 23 |  | One or more doors are open.
bitfield32 | Evt1 |  |  | Name: CURRENT_IMBALANCE_WARNING; Label: Current Imbalance Warning; Value: 24 |  | A current imbalance exists between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: OTHER_ALARM; Label: Other Battery Alarm; Value: 25 |  | A vendor specific alarm has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | Evt1 |  |  | Name: OTHER_WARNING; Label: Other Battery Warning; Value: 26 |  | A vendor specific warning has occurred. | See EvtVnd1 and EvtVnd2 for more information.
enum16 | ReqInvState |  |  | Name: NO REQUEST; Label: No Request; Value: 0 |  | Battery has no requests of the inverter.
enum16 | ReqInvState |  |  | Name: START; Label: Start Inverter; Value: 1 |  | Battery requests that the inverter be started. | Battery is notified of inverter state change through SetInvState.
enum16 | ReqInvState |  |  | Name: STOP; Label: Stop Inverter; Value: 2 |  | Battery requests that the inverter be stopped. | Battery is notified of inverter state change through SetInvState.
enum16 | SetOp |  |  | Name: CONNECT; Label: Connect the Battery Bank; Value: 1 |  | Initialize the battery bank and close contactors for all enabled strings.
enum16 | SetOp |  |  | Name: DISCONNECT; Label: Disconnect the Battery Bank; Value: 2 |  | Open contactors for all strings.
enum16 | SetInvState |  |  | Name: INVERTER_STOPPED; Label: Inverter is Stopped; Value: 1
enum16 | SetInvState |  |  | Name: INVERTER_STANDBY; Label: Inverter is in Standby; Value: 2
enum16 | SetInvState |  |  | Name: INVERTER_STARTED; Label: Inverter is Started; Value: 3

## 804
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Lithium-Ion String Model | 804 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 46 + (RB Count * 16) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Idx | String Index |  | uint16 |  |  | R | M | Index of the string within the bank. | Indices are one-based.
Fixed Block |  | 3 | 1 | 1 | NMod | Module Count |  | uint16 |  |  | R | M | Count of modules in the string.
Fixed Block |  | 4 | 2 | 2 | St | String Status |  | bitfield32 |  |  | R | M | Current status of the string.
Fixed Block |  | 6 | 4 | 1 | ConFail | Connection Failure Reason |  | enum16 |  |  | R | O
Fixed Block |  | 7 | 5 | 1 | NCellBal | String Cell Balancing Count |  | uint16 |  |  | R | O | Number of cells currently being balanced in the string.
Fixed Block |  | 8 | 6 | 1 | SoC | String State of Charge |  | uint16 | % | SoC_SF | R | M | Battery string state of charge, expressed as a percentage. | Measurement.
Fixed Block |  | 9 | 7 | 1 | DoD | String Depth of Discharge |  | uint16 | % | DoD_SF | R | O | Depth of discharge for the string, expressed as a percentage. | Measurement.
Fixed Block |  | 10 | 8 | 2 | NCyc | String Cycle Count |  | uint32 |  |  | R | O | Number of discharge cycles executed upon the string.
Fixed Block |  | 12 | 10 | 1 | SoH | String State of Health |  | uint16 | % | SoH_SF | R | O | Battery string state of health, expressed as a percentage. | Measurement.
Fixed Block |  | 13 | 11 | 1 | A | String Current |  | int16 | A | A_SF | R | M | String current measurement. | Measurement.
Fixed Block |  | 14 | 12 | 1 | V | String Voltage |  | uint16 | V | V_SF | R | O | String voltage measurement. | Measurement.
Fixed Block |  | 15 | 13 | 1 | CellVMax | Max Cell Voltage |  | uint16 | V | CellV_SF | R | M | Maximum voltage for all cells in the string. | Measurement.
Fixed Block |  | 16 | 14 | 1 | CellVMaxMod | Max Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with maximum cell voltage.
Fixed Block |  | 17 | 15 | 1 | CellVMin | Min Cell Voltage |  | uint16 | V | CellV_SF | R | M | Minimum voltage for all cells in the string. | Measurement.
Fixed Block |  | 18 | 16 | 1 | CellVMinMod | Min Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with minimum cell voltage.
Fixed Block |  | 19 | 17 | 1 | CellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | M | Average voltage for all cells in the string. | Calculation based on measurements.
Fixed Block |  | 20 | 18 | 1 | ModTmpMax | Max Module Temperature |  | int16 | C | ModTmp_SF | R | M | Maximum temperature for all modules in the string. | Measurement.
Fixed Block |  | 21 | 19 | 1 | ModTmpMaxMod | Max Module Temperature Module |  | uint16 |  |  | R | M | Module with the maximum temperature.
Fixed Block |  | 22 | 20 | 1 | ModTmpMin | Min Module Temperature |  | int16 | C | ModTmp_SF | R | M | Minimum temperature for all modules in the string. | Measurement.
Fixed Block |  | 23 | 21 | 1 | ModTmpMinMod | Min Module Temperature Module |  | uint16 |  |  | R | M | Module with the minimum temperature.
Fixed Block |  | 24 | 22 | 1 | ModTmpAvg | Average Module Temperature |  | int16 | C | ModTmp_SF | R | M | Average temperature for all modules in the string. | Calculation based on measurements.
Fixed Block |  | 25 | 23 | 1 | Pad1 | Pad |  | pad |  |  | R | M | Pad register.
Fixed Block |  | 26 | 24 | 2 | ConSt | Contactor Status |  | bitfield32 |  |  | R | O | Status of the contactor(s) for the string.
Fixed Block |  | 28 | 26 | 2 | Evt1 | String Event 1 |  | bitfield32 |  |  | R | M | Alarms, warnings and status values. Bit flags.
Fixed Block |  | 30 | 28 | 2 | Evt2 | String Event 2 |  | bitfield32 |  |  | R | O | Alarms, warnings and status values. Bit flags. | Reserved for future use.
Fixed Block |  | 32 | 30 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events.
Fixed Block |  | 34 | 32 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events.
Fixed Block |  | 36 | 34 | 1 | SetEna | Enable/Disable String |  | enum16 |  |  | RW | O | Enables and disables the string. Should reset to 0 upon completion.
Fixed Block |  | 37 | 35 | 1 | SetCon | Connect/Disconnect String |  | enum16 |  |  | RW | O | Connects and disconnects the string. | Should reset to 0 upon completion.
Fixed Block |  | 38 | 36 | Size: 1; Name: SoC_SF; Type: sunssf; R/W: R | M | Scale factor for string state of charge.
Fixed Block |  | 39 | 37 | Size: 1; Name: SoH_SF; Type: sunssf; R/W: R | O | Scale factor for string state of health.
Fixed Block |  | 40 | 38 | Size: 1; Name: DoD_SF; Type: sunssf; R/W: R | O | Scale factor for string depth of discharge.
Fixed Block |  | 41 | 39 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Scale factor for string current.
Fixed Block |  | 42 | 40 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | O | Scale factor for string voltage.
Fixed Block |  | 43 | 41 | Size: 1; Name: CellV_SF; Type: sunssf; R/W: R | M | Scale factor for cell voltage.
Fixed Block |  | 44 | 42 | Size: 1; Name: ModTmp_SF; Type: sunssf; R/W: R | M | Scale factor for module temperature.
Fixed Block |  | 45 | 43 | 1 | Pad2 | Pad |  | pad |  |  | R | M | Pad register.
Fixed Block |  | 46 | 44 | 1 | Pad3 | Pad |  | pad |  |  | R | M | Pad register.
Fixed Block |  | 47 | 45 | 1 | Pad4 | Pad |  | pad |  |  | R | M | Pad register.
Repeating Block |  | 48 | 0 | 1 | ModNCell | Module Cell Count |  | uint16 |  |  | R | M | Count of all cells in the module.
Repeating Block |  | 49 | 1 | 1 | ModSoC | Module SoC |  | uint16 | % | SoC_SF | R | O | Module state of charge, expressed as a percentage.
Repeating Block |  | 50 | 2 | 1 | ModSoH | Module SoH |  | uint16 | % | SoH_SF | R | O | Module state of health, expressed as a percentage.
Repeating Block |  | 51 | 3 | 1 | ModCellVMax | Max Cell Voltage |  | uint16 | V | CellV_SF | R | M | Maximum voltage for all cells in the module. | Measurement.
Repeating Block |  | 52 | 4 | 1 | ModCellVMaxCell | Max Cell Voltage Cell |  | uint16 |  |  | R | O | Cell with maximum voltage.
Repeating Block |  | 53 | 5 | 1 | ModCellVMin | Min Cell Voltage |  | uint16 | V | CellV_SF | R | M | Minimum voltage for all cells in the module. | Measurement.
Repeating Block |  | 54 | 6 | 1 | ModCellVMinCell | Min Cell Voltage Cell |  | uint16 | V | CellV_SF | R | O | Cell with minimum voltage.
Repeating Block |  | 55 | 7 | 1 | ModCellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | M | Average voltage for all cells in the module. | Calculation based on measurements.
Repeating Block |  | 56 | 8 | 1 | ModCellTmpMax | Max Cell Temperature |  | int16 | C | ModTmp_SF | R | M | Maximum temperature for all cells in the module. | Measurement.
Repeating Block |  | 57 | 9 | 1 | ModCellTmpMaxCell | Max Cell Temperature Cell |  | uint16 |  |  | R | O | Cell with maximum temperature.
Repeating Block |  | 58 | 10 | 1 | ModCellTmpMin | Min Cell Temperature |  | int16 | C | ModTmp_SF | R | M | Minimum temperature for all cells in the module. | Measurement.
Repeating Block |  | 59 | 11 | 1 | ModCellTmpMinCell | Min Cell Temperature Cell |  | uint16 |  |  | R | O | Cell with minimum temperature.
Repeating Block |  | 60 | 12 | 1 | ModCellTmpAvg | Average Cell Temperature |  | int16 | C | ModTmp_SF | R | M | Average temperature for all cells in the module. | Calculation based on measurements.
Repeating Block |  | 61 | 13 | 1 | Pad5 | Pad |  | pad |  |  | R | M | Pad register.
Repeating Block |  | 62 | 14 | 1 | Pad6 | Pad |  | pad |  |  | R | M | Pad register.
Repeating Block |  | 63 | 15 | 1 | Pad7 | Pad |  | pad |  |  | R | M | Pad register.
bitfield32 | St |  |  | Name: STRING_ENABLED; Label: String Is Enabled; Value: 0 |  | String is enabled and will connect next time battery is asked to connect.
bitfield32 | St |  |  | Name: CONTACTOR_STATUS; Label: Contactor Status; Value: 1 |  | String contactor is closed. | If string has multiple contactors, indicates that all contactors are closed.
enum16 | ConFail |  |  | Name: NO_FAILURE; Label: No Failure; Value: 0 |  | Connect did not fail.
enum16 | ConFail |  |  | Name: BUTTON_PUSHED; Label: Button Pushed; Value: 1 |  | A button was pushed which prevented connection.
enum16 | ConFail |  |  | Name: STR_GROUND_FAULT; Label: Ground Fault; Value: 2 |  | Ground fault during auto-connect.
enum16 | ConFail |  |  | Name: OUTSIDE_VOLTAGE_RANGE; Label: Outside Voltage Range; Value: 3 |  | Outside voltage target window during auto-connect.
enum16 | ConFail |  |  | Name: STRING_NOT_ENABLED; Label: String Not Enabled; Value: 4 |  | The string is not enabled.
enum16 | ConFail |  |  | Name: FUSE_OPEN; Label: Fuse Open; Value: 5 |  | A fuse is open which prevents connection.
enum16 | ConFail |  |  | Name: CONTACTOR_FAILURE; Label: Contactor Failure; Value: 6 |  | A contactor failed to operate.
enum16 | ConFail |  |  | Name: PRECHARGE_FAILURE; Label: Precharge Failure; Value: 7 |  | A precharge failure occurred.
enum16 | ConFail |  |  | Name: STRING_FAULT; Label: String Fault; Value: 8 |  | A string fault has occurred. | See Evt1 for more information.
bitfield32 | ConSt |  |  | Name: CONTACTOR_0; Label: Contactor 0 Closed; Value: 0
bitfield32 | ConSt |  |  | Name: CONTACTOR_1; Label: Contactor 1 Closed; Value: 1
bitfield32 | ConSt |  |  | Name: CONTACTOR_2; Label: Contactor 2 Closed; Value: 2
bitfield32 | ConSt |  |  | Name: CONTACTOR_3; Label: Contactor 3 Closed; Value: 3
bitfield32 | ConSt |  |  | Name: CONTACTOR_4; Label: Contactor 4 Closed; Value: 4
bitfield32 | ConSt |  |  | Name: CONTACTOR_5; Label: Contactor 5 Closed; Value: 5
bitfield32 | ConSt |  |  | Name: CONTACTOR_6; Label: Contactor 6 Closed; Value: 6
bitfield32 | ConSt |  |  | Name: CONTACTOR_7; Label: Contactor 7 Closed; Value: 7
bitfield32 | ConSt |  |  | Name: CONTACTOR_8; Label: Contactor 8 Closed; Value: 8
bitfield32 | ConSt |  |  | Name: CONTACTOR_9; Label: Contactor 9 Closed; Value: 9
bitfield32 | ConSt |  |  | Name: CONTACTOR_10; Label: Contactor 10 Closed; Value: 10
bitfield32 | ConSt |  |  | Name: CONTACTOR_11; Label: Contactor 11 Closed; Value: 11
bitfield32 | ConSt |  |  | Name: CONTACTOR_12; Label: Contactor 12 Closed; Value: 12
bitfield32 | ConSt |  |  | Name: CONTACTOR_13; Label: Contactor 13 Closed; Value: 13
bitfield32 | ConSt |  |  | Name: CONTACTOR_14; Label: Contactor 14 Closed; Value: 14
bitfield32 | ConSt |  |  | Name: CONTACTOR_15; Label: Contactor 15 Closed; Value: 15
bitfield32 | ConSt |  |  | Name: CONTACTOR_16; Label: Contactor 16 Closed; Value: 16
bitfield32 | ConSt |  |  | Name: CONTACTOR_17; Label: Contactor 17 Closed; Value: 17
bitfield32 | ConSt |  |  | Name: CONTACTOR_18; Label: Contactor 18 Closed; Value: 18
bitfield32 | ConSt |  |  | Name: CONTACTOR_19; Label: Contactor 19 Closed; Value: 19
bitfield32 | ConSt |  |  | Name: CONTACTOR_20; Label: Contactor 20 Closed; Value: 20
bitfield32 | ConSt |  |  | Name: CONTACTOR_21; Label: Contactor 21 Closed; Value: 21
bitfield32 | ConSt |  |  | Name: CONTACTOR_22; Label: Contactor 22 Closed; Value: 22
bitfield32 | ConSt |  |  | Name: CONTACTOR_23; Label: Contactor 23 Closed; Value: 23
bitfield32 | ConSt |  |  | Name: CONTACTOR_24; Label: Contactor 24 Closed; Value: 24
bitfield32 | ConSt |  |  | Name: CONTACTOR_25; Label: Contactor 25 Closed; Value: 25
bitfield32 | ConSt |  |  | Name: CONTACTOR_26; Label: Contactor 26 Closed; Value: 26
bitfield32 | ConSt |  |  | Name: CONTACTOR_27; Label: Contactor 27 Closed; Value: 27
bitfield32 | ConSt |  |  | Name: CONTACTOR_28; Label: Contactor 28 Closed; Value: 28
bitfield32 | ConSt |  |  | Name: CONTACTOR_29; Label: Contactor 29 Closed; Value: 29
bitfield32 | ConSt |  |  | Name: CONTACTOR_30; Label: Contactor 30 Closed; Value: 30
bitfield32 | Evt1 |  |  | Name: COMMUNICATION_ERROR; Label: Communication Error; Value: 0 |  | String is unable to communicate with battery modules.
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_ALARM; Label: Over Temperature Alarm; Value: 1 |  | Battery string has exceeded maximum operating temperature
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_WARNING; Label: Over Temperature Warning; Value: 2 |  | Battery string is approaching maximum operating temperature.
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_ALARM; Label: Under Temperature Alarm; Value: 3 |  | Battery string has exceeded minimum operating temperature
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_WARNING; Label: Under Temperature Warning; Value: 4 |  | Battery string is approaching minimum operating temperature.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_ALARM; Label: Over Charge Current Alarm; Value: 5 |  | Battery string maximum charge current has been exceeded. | See AChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_WARNING; Label: Over Charge Current Warning; Value: 6 |  | Approaching battery string maximum charge current. | See AChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_ALARM; Label: Over Discharge Current Alarm; Value: 7 |  | Battery string maximum discharge current has been exceeded. | See ADisChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_WARNING; Label: Over Discharge Current Warning; Value: 8 |  | Approaching battery string maximum discharge current. | See ADisChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_ALARM; Label: Over Voltage Alarm; Value: 9 |  | Battery string voltage has exceeded maximum limit.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_WARNING; Label: Over Voltage Warning; Value: 10 |  | Battery string voltage is approaching maximum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_ALARM; Label: Under Voltage Alarm; Value: 11 |  | Battery string voltage has exceeded minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_WARNING; Label: Under Voltage Warning; Value: 12 |  | Battery string voltage is approaching minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_ALARM; Label: Under State of Charge Min Alarm; Value: 13 |  | Battery string state of charge has reached or exceeded SoCMin.
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_WARNING; Label: Under State of Charge Min Warning; Value: 14 |  | Battery string state of charge is approaching SoCMin.
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_ALARM; Label: Over State of Charge Max Alarm; Value: 15 |  | Battery string state of charge has reached or exceeded SoCMax.
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_WARNING; Label: Over State of Charge Max Warning; Value: 16 |  | Battery string state of charge is approaching SoCMax.
bitfield32 | Evt1 |  |  | Name: VOLTAGE_IMBALANCE_WARNING; Label: Voltage Imbalance Warning; Value: 17 |  | A voltage imbalance exists between the modules in the battery string.
bitfield32 | Evt1 |  |  | Name: TEMPERATURE_IMBALANCE_ALARM; Label: Temperature Imbalance Alarm; Value: 18 |  | A temperature imbalance exists between the modules in the battery string.
bitfield32 | Evt1 |  |  | Name: TEMPERATURE_IMBALANCE_WARNING; Label: Temperature Imbalance Warning; Value: 19 |  | A temperature imbalance is developing between the modules in the battery string.
bitfield32 | Evt1 |  |  | Name: CONTACTOR_ERROR; Label: Contactor Error; Value: 20 |  | A contactor failed to open or close as requested.
bitfield32 | Evt1 |  |  | Name: FAN_ERROR; Label: Fan Error; Value: 21 |  | One or more battery fans has failed.
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground Fault Error; Value: 22 |  | Ground fault detected.
bitfield32 | Evt1 |  |  | Name: OPEN_DOOR_ERROR; Label: Open Door Error; Value: 23 |  | One or more doors are open.
bitfield32 | Evt1 |  |  | Name: RESERVED_1; Label: Reserved; Value: 24 |  | Reserved bit. | Do not implement.
bitfield32 | Evt1 |  |  | Name: OTHER_ALARM; Label: Other String Alarm; Value: 25 |  | A vendor specific alarm has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | Evt1 |  |  | Name: OTHER_WARNING; Label: Other String Warning; Value: 26 |  | A vendor specific warning has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | Evt1 |  |  | Name: RESERVED_2; Label: Reserved; Value: 27 |  | Reserved bit. | Do not implement.
bitfield32 | Evt1 |  |  | Name: CONFIGURATION_ALARM; Label: Configuation Alarm; Value: 28 |  | The battery string has been configured incorrectly and will not operate as expected.
bitfield32 | Evt1 |  |  | Name: CONFIGURATION_WARNING; Label: Configuation Warning; Value: 29 |  | The battery string has been configured incorrectly and may not operate as expected.
enum16 | SetEna |  |  | Name: DISABLED; Value: 0
enum16 | SetEna |  |  | Name: ENABLED; Value: 1
enum16 | SetCon |  |  | Name: CONNECT_STRING; Label: Connect String; Value: 1 |  | Connect the string.
enum16 | SetCon |  |  | Name: DISCONNECT_STRING; Label: Disconnect String; Value: 2 |  | Disconnect the string.

## 64207
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | REbus Status | 64207 | uint16 |  |  | R | M | REbus status data that is defined commonly across Pika Energy REbus devices
Header |  | 1 |  | 1 | L |  | 12 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | P | REbus Power |  | int16 | W |  | R | M | REbus power. Positive indicates the device is sourcing to REbus, and negative indicates sinking from REbus.
Fixed Block |  | 3 | 1 | 2 | E | Accumulated Energy |  | uint32 | Wh |  | R | M | Total accumulated energy (exact definition differs by device)
Fixed Block |  | 5 | 3 | 1 | V | REbus Voltage |  | uint16 | V | VT_sf | R | M | REbus DC Bus Voltage
Fixed Block |  | 6 | 4 | 1 | I | REbus Current |  | int16 | A | I_sf | R | M | REbus current. Positive indicates the device is sourcing to REbus, and negative indicates sinking from REbus.
Fixed Block |  | 7 | 5 | 1 | T | Device Temperature |  | int16 | Deg C | VT_sf | R | M | Device temperature
Fixed Block |  | 8 | 6 | 1 | St | State |  | enum16 |  |  | R | M |  | State is a status field used by Pika Energy for operations and maintenance purposes
Fixed Block |  | 9 | 7 | 1 | Ev | Last Event |  | enum16 |  |  | R | M |  | The most recent event that occurred on the device
Fixed Block |  | 10 | 8 | 1 | RB | REbusBits |  | bitfield16 |  |  | R | M | REbus status register
Fixed Block |  | 11 | 9 | 1 | VT_sf | VT_sf |  | sunssf |  |  | R | M | Scale factor for V and T
Fixed Block |  | 12 | 10 | 1 | I_sf | I_sf |  | sunssf |  |  | R | M | Scale factor for I
Fixed Block |  | 13 | 11 | Size: 1; Name: Pad0; Type: pad; R/W: R | M
enum16 | St |  |  | Name: UNKNOWN; Label: device offline; Value: 0
enum16 | St |  |  | Name: DISABLED; Label: disabled; Value: 16
enum16 | St |  |  | Name: INITIALIZING; Label: initializing; Value: 256
enum16 | St |  |  | Name: POWERING_UP; Label: powering up; Value: 272
enum16 | St |  |  | Name: CONNECTING_BUS; Label: connecting to REbus; Value: 288
enum16 | St |  |  | Name: DISCONNECTING_BUS; Label: disconnecting REbus; Value: 304
enum16 | St |  |  | Name: TESTING_BUS; Label: testing REbus...; Value: 320
enum16 | St |  |  | Name: LOW_BUS_VOLTAGE; Label: low REbus voltage; Value: 512
enum16 | St |  |  | Name: STANDBY; Label: standby; Value: 768
enum16 | St |  |  | Name: WAITING; Label: waiting; Value: 784
enum16 | St |  |  | Name: WAITING_NO_INPUT; Label: waiting - no input; Value: 800
enum16 | St |  |  | Name: CONNECTING_GRID; Label: connecting grid; Value: 2048
enum16 | St |  |  | Name: DISCONNECTING_GRID; Label: disconnecting grid; Value: 2064
enum16 | St |  |  | Name: GRID_CONNECTED; Label: grid connected; Value: 2080
enum16 | St |  |  | Name: ISLANDED; Label: islanded; Value: 2096
enum16 | St |  |  | Name: CONNECTING_GENERATOR; Label: connecting generator; Value: 2112
enum16 | St |  |  | Name: GENERATOR_PARALLEL; Label: generator parallel; Value: 2128
enum16 | St |  |  | Name: LOW_INPUT_VOLTAGE; Label: low input voltage; Value: 4096
enum16 | St |  |  | Name: TESTING_DEVICE_INPUT; Label: testing input...; Value: 4112
enum16 | St |  |  | Name: CONNECTING_INPUT; Label: connecting input; Value: 4352
enum16 | St |  |  | Name: DISCONNECTING_INPUT; Label: disconnecting input; Value: 4368
enum16 | St |  |  | Name: CALIBRATING; Label: calibrating; Value: 4608
enum16 | St |  |  | Name: CALIBRATION_SUCCESS; Label: calibration success!; Value: 4624
enum16 | St |  |  | Name: CALIBRATION_NEEDED; Label: calibration required; Value: 4640
enum16 | St |  |  | Name: BURN_IN; Label: burning in; Value: 4656
enum16 | St |  |  | Name: BURN_IN_DONE; Label: burn in done; Value: 4672
enum16 | St |  |  | Name: SCHEDULER_OVERRIDDEN; Label: running, overridden; Value: 4864
enum16 | St |  |  | Name: SCHEDULER_DISABLED; Label: scheduler disabled; Value: 4880
enum16 | St |  |  | Name: RUNNING; Label: running; Value: 8192
enum16 | St |  |  | Name: MAKING_POWER; Label: making power; Value: 8208
enum16 | St |  |  | Name: LIMITING_POWER; Label: limiting power; Value: 6
enum16 | St |  |  | Name: LOW_WIND; Label: low wind; Value: 12288
enum16 | St |  |  | Name: HIGH_WIND; Label: high wind; Value: 12304
enum16 | St |  |  | Name: LOW_SUN; Label: low sun; Value: 12544
enum16 | St |  |  | Name: CHARGING_BATTERY; Label: charging; Value: 24576
enum16 | St |  |  | Name: FLOAT_CHARGING_BATTERY; Label: float charging; Value: 24592
enum16 | St |  |  | Name: BULK_CHARGING_BATTERY; Label: bulk charging; Value: 24608
enum16 | St |  |  | Name: ABSORPTION_CHARGING_BATTERY; Label: absorption charging; Value: 24624
enum16 | St |  |  | Name: EQUALIZE_CHARGING_BATTERY; Label: equalizing; Value: 24640
enum16 | St |  |  | Name: DISCHARGING_BATTERY; Label: discharging; Value: 24832
enum16 | St |  |  | Name: LOW_BATTERY_VOLTAGE; Label: low battery voltage; Value: 24848
enum16 | St |  |  | Name: ERROR_GENERIC; Label: error; Value: 28672
enum16 | St |  |  | Name: OVER_VOLTAGE_INPUT; Label: over voltage input; Value: 28688
enum16 | St |  |  | Name: OVER_VOLTAGE_OUTPUT; Label: over voltage output; Value: 28704
enum16 | St |  |  | Name: OVER_CURRENT_INPUT; Label: over current input; Value: 28720
enum16 | St |  |  | Name: OVER_CURRENT_OUTPUT; Label: over current output; Value: 28736
enum16 | St |  |  | Name: ERROR_LOW_BATTERY_VOLTAGE; Label: error: low batt volts; Value: 28752
enum16 | St |  |  | Name: OVER_TEMPERATURE; Label: over temp shutdown; Value: 41216
enum16 | St |  |  | Name: GROUND_FAULT; Label: ground fault; Value: 49152
enum16 | St |  |  | Name: INSULATION_FAULT; Label: err: insulation fault; Value: 29200
enum16 | St |  |  | Name: CALIBRATION_0; Label: calibration mode; Value: 32256
enum16 | St |  |  | Name: CALIBRATION_1; Label: calibration 1; Value: 32272
enum16 | St |  |  | Name: CALIBRATION_2; Label: calibration 2; Value: 32288
enum16 | St |  |  | Name: CALIBRATION_3; Label: calibration 3; Value: 32304
enum16 | Ev |  |  | Name: GENERIC; Label: unknown event; Value: 32768
enum16 | Ev |  |  | Name: POWERUP; Label: power up; Value: 32784
enum16 | Ev |  |  | Name: SUPPLY_UNDERVOLTAGE; Label: supply under voltage; Value: 32800
enum16 | Ev |  |  | Name: DAILY_EVENT; Label: daily event; Value: 32816
enum16 | Ev |  |  | Name: ENABLE; Label: enable; Value: 33024
enum16 | Ev |  |  | Name: DISABLE; Label: disable; Value: 33280
enum16 | Ev |  |  | Name: MANUAL_DISABLE; Label: manual disable; Value: 33296
enum16 | Ev |  |  | Name: EXTERNAL_ESTOP; Label: external estop; Value: 33312
enum16 | Ev |  |  | Name: SYSMODE_CHANGE; Label: sysmode change; Value: 33536
enum16 | Ev |  |  | Name: SYSMODE_BAD; Label: unauthorized sysmode; Value: 33792
enum16 | Ev |  |  | Name: DEBUG_TRACE; Label: debug trace recorded; Value: 34048
enum16 | Ev |  |  | Name: TOU_ENTRY_ACTIVATED; Label: TOU entry activated; Value: 34304
enum16 | Ev |  |  | Name: SOFTWARE_VERSION; Label: software version; Value: 36832
enum16 | Ev |  |  | Name: HARDWARE_VERSION; Label: hardware version mismatch; Value: 36848
enum16 | Ev |  |  | Name: INTERRUPT_FAULT; Label: interrupt fault; Value: 36864
enum16 | Ev |  |  | Name: GATEDRIVE_FAULT; Label: gate drive fault; Value: 37120
enum16 | Ev |  |  | Name: TIMER_FAULT; Label: timer fault; Value: 37376
enum16 | Ev |  |  | Name: TRANSISTOR_FAILURE; Label: transistor failure; Value: 39168
enum16 | Ev |  |  | Name: OVER_TEMPERATURE; Label: over temp shutdown; Value: 41216
enum16 | Ev |  |  | Name: FAN_FAILURE; Label: fan failure; Value: 41232
enum16 | Ev |  |  | Name: FUSE_BLOWN; Label: fuse blown; Value: 41248
enum16 | Ev |  |  | Name: MISWIRING; Label: miswiring fault; Value: 41472
enum16 | Ev |  |  | Name: ALTERNATOR_BAD; Label: alternator bad; Value: 42496
enum16 | Ev |  |  | Name: REVERSE_ROTATION; Label: reverse rotation; Value: 42752
enum16 | Ev |  |  | Name: BUS_FAULT; Label: REbus fault; Value: 45056
enum16 | Ev |  |  | Name: BUS_NO_LOAD; Label: REbus no load; Value: 45072
enum16 | Ev |  |  | Name: BUS_OVER_VOLTAGE; Label: REbus over voltage; Value: 45312
enum16 | Ev |  |  | Name: BUS_UNDER_VOLTAGE; Label: REbus under voltage; Value: 45328
enum16 | Ev |  |  | Name: BUS_OVER_CURRENT; Label: REbus over current; Value: 45568
enum16 | Ev |  |  | Name: INTERNAL_OVERVOLTAGE; Label: internal over voltage; Value: 45824
enum16 | Ev |  |  | Name: BATTERY_GENERIC; Label: battery generic; Value: 47104
enum16 | Ev |  |  | Name: BATTERY_READY; Label: battery ready; Value: 47120
enum16 | Ev |  |  | Name: BATTERY_NOT_READY; Label: battery not ready; Value: 47136
enum16 | Ev |  |  | Name: BMS_GENERIC; Label: BMS generic; Value: 47360
enum16 | Ev |  |  | Name: BMS_ALARM; Label: BMS alarm; Value: 47376
enum16 | Ev |  |  | Name: BMS_WARNING; Label: BMS warning; Value: 47392
enum16 | Ev |  |  | Name: BMS_ERROR; Label: BMS error; Value: 47408
enum16 | Ev |  |  | Name: GROUND_FAULT; Label: ground fault; Value: 49152
enum16 | Ev |  |  | Name: INPUT_LOW; Label: input low; Value: 49408
enum16 | Ev |  |  | Name: INPUT_SENSOR_FAULT; Label: input sensor fault; Value: 49664
enum16 | Ev |  |  | Name: INPUT_OVER_CURRENT; Label: input over current; Value: 49920
enum16 | Ev |  |  | Name: INPUT_OVERSPEED; Label: input overspeed; Value: 50176
enum16 | Ev |  |  | Name: INPUT_HIGH; Label: input high; Value: 50432
enum16 | Ev |  |  | Name: ARC_FAULT; Label: arc fault; Value: 50688
enum16 | Ev |  |  | Name: INPUT_READY; Label: input ready; Value: 50944
enum16 | Ev |  |  | Name: GRID_FAULT; Label: grid fault; Value: 53248
enum16 | Ev |  |  | Name: GRID_OVER_VOLTAGE; Label: grid over voltage; Value: 53264
enum16 | Ev |  |  | Name: GRID_OVER_CURRENT; Label: grid over current; Value: 53280
enum16 | Ev |  |  | Name: GRID_OVER_FREQUENCY; Label: grid over frequency; Value: 53296
enum16 | Ev |  |  | Name: GRID_UNDER_VOLTAGE; Label: grid under voltage; Value: 53312
enum16 | Ev |  |  | Name: GRID_UNDER_FREQUENCY; Label: grid under frequency; Value: 53328
enum16 | Ev |  |  | Name: GRID_OVER_VOLTAGE_FAST; Label: grid overvoltage fast; Value: 53344
enum16 | Ev |  |  | Name: GRID_HIGH_IMPEDANCE; Label: grid high impedance; Value: 53360
enum16 | Ev |  |  | Name: TRANSFER_FAIL; Label: transfer sw fail; Value: 53504
enum16 | Ev |  |  | Name: SETPOINT_CRC_FAULT; Label: setpoint crc fault; Value: 57344
enum16 | Ev |  |  | Name: EEPROM_FAULT; Label: EEPROM failure; Value: 57600
enum16 | Ev |  |  | Name: FLASH_FAULT; Label: FLASH fault; Value: 57856
enum16 | Ev |  |  | Name: PLM_RESTART; Label: PLM restart; Value: 58112
enum16 | Ev |  |  | Name: DEFAULT_TRAP; Label: default trap; Value: 61440
enum16 | Ev |  |  | Name: ADDRESS_ERROR; Label: address error trap; Value: 61456
enum16 | Ev |  |  | Name: STACK_ERROR; Label: stack error trap; Value: 61472
enum16 | Ev |  |  | Name: OSCILLATOR_FAIL; Label: osc. fail trap; Value: 61488
enum16 | Ev |  |  | Name: MATH_ERROR; Label: math error trap; Value: 61504
enum16 | Ev |  |  | Name: DMAC_ERROR; Label: dmac error trap; Value: 61520
bitfield16 | RB |  |  | Name: ENABLE_MASTER; Value: 0
bitfield16 | RB |  |  | Name: ENABLE_SOURCE; Value: 1
bitfield16 | RB |  |  | Name: ENABLE_SINK; Value: 2
bitfield16 | RB |  |  | Name: REBUS_CONNECTED; Value: 3
bitfield16 | RB |  |  | Name: SOURCING; Value: 4
bitfield16 | RB |  |  | Name: SINKING; Value: 5
bitfield16 | RB |  |  | Name: LIMITING_POWER; Label: limiting power; Value: 6
bitfield16 | RB |  |  | Name: TEMP_LIMIT; Value: 7
bitfield16 | RB |  |  | Name: BUS_VOLTAGE_LOW; Value: 8
bitfield16 | RB |  |  | Name: DEV_VOLTAGE_LOW; Value: 9
bitfield16 | RB |  |  | Name: BUS_VOLTAGE_HIGH; Value: 10
bitfield16 | RB |  |  | Name: DEV_VOLTAGE_HIGH; Value: 11
bitfield16 | RB |  |  | Name: TEMPERATURE_HIGH; Value: 12
bitfield16 | RB |  |  | Name: SPT_INVALID; Value: 13
bitfield16 | RB |  |  | Name: GROUNDFAULT; Value: 14
bitfield16 | RB |  |  | Name: SUPPLY_VOLTAGE_LOW; Value: 15

## 64209
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Pika Energy B-Link Status | 64209 | uint16 |  |  | R | M | Miscellaneous battery status registers
Header |  | 1 |  | 1 | L |  | 22 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | WhIn | Total Energy In |  | uint32 | Wh |  | R | M | Energy absorbed by battery
Fixed Block |  | 4 | 2 | 2 | WhOut | Total Energy Out |  | uint32 | Wh |  | R | M | Energy supplied by battery
Fixed Block |  | 6 | 4 | 1 | ErrorWord | Error status |  | bitfield16 |  |  | R | M | Error status bitfield
Fixed Block |  | 7 | 5 | 1 | EnableBits | Enable bits |  | bitfield16 |  |  | R | M | Internal status register
Fixed Block |  | 8 | 6 | 1 | InhibitBits | InhibitBits |  | bitfield16 |  |  | R | M | Internal status register
Fixed Block |  | 9 | 7 | 1 | StatusBits | General Status |  | bitfield16 |  |  | R | M | General system status
Fixed Block |  | 10 | 8 | 1 | BMSStatus | BMS Status |  | bitfield16 |  |  | R | M | Battery Management System flags
Fixed Block |  | 11 | 9 | 1 | Pad0 | Pad |  | pad |  |  | R | M | Large pad for future model expansion
Fixed Block |  | 12 | 10 | Size: 1; Name: Pad1; Type: pad; R/W: R | M
Fixed Block |  | 13 | 11 | Size: 1; Name: Pad2; Type: pad; R/W: R | M
Fixed Block |  | 14 | 12 | Size: 1; Name: Pad3; Type: pad; R/W: R | M
Fixed Block |  | 15 | 13 | Size: 1; Name: Pad4; Type: pad; R/W: R | M
Fixed Block |  | 16 | 14 | Size: 1; Name: Pad5; Type: pad; R/W: R | M
Fixed Block |  | 17 | 15 | Size: 1; Name: Pad6; Type: pad; R/W: R | M
Fixed Block |  | 18 | 16 | Size: 1; Name: Pad7; Type: pad; R/W: R | M
Fixed Block |  | 19 | 17 | Size: 1; Name: Pad8; Type: pad; R/W: R | M
Fixed Block |  | 20 | 18 | Size: 1; Name: Pad9; Type: pad; R/W: R | M
Fixed Block |  | 21 | 19 | Size: 1; Name: Pad10; Type: pad; R/W: R | M
Fixed Block |  | 22 | 20 | Size: 1; Name: Pad11; Type: pad; R/W: R | M
Fixed Block |  | 23 | 21 | Size: 1; Name: Pad12; Type: pad; R/W: R | M
bitfield16 | ErrorWord |  |  | Name: CS_ZERO_ERR; Value: 0
bitfield16 | ErrorWord |  |  | Name: REF_FAIL; Value: 1
bitfield16 | ErrorWord |  |  | Name: THERM_FAIL; Value: 2
bitfield16 | ErrorWord |  |  | Name: UNUSED; Value: 11
bitfield16 | ErrorWord |  |  | Name: EEPROM_FAIL; Value: 4
bitfield16 | ErrorWord |  |  | Name: SPT_ERROR; Value: 5
bitfield16 | ErrorWord |  |  | Name: HWV_MISMATCH; Value: 6
bitfield16 | ErrorWord |  |  | Name: SPTV_MISMATCH; Value: 7
bitfield16 | ErrorWord |  |  | Name: BATT_OVERTEMP; Value: 8
bitfield16 | ErrorWord |  |  | Name: REPEAT_OVERCURRENT; Value: 9
bitfield16 | ErrorWord |  |  | Name: FAN_FAIL; Value: 10
bitfield16 | ErrorWord |  |  | Name: CURRENT_CTRL_FAIL; Value: 11
bitfield16 | ErrorWord |  |  | Name: BMS_ERROR; Value: 12
bitfield16 | ErrorWord |  |  | Name: REPEAT_CONTACT; Value: 13
bitfield16 | ErrorWord |  |  | Name: EXTERNAL_STOP; Value: 14
bitfield16 | ErrorWord |  |  | Name: GROUND_FAULT; Value: 15
bitfield16 | EnableBits |  |  | Name: DEADMAN; Value: 0
bitfield16 | EnableBits |  |  | Name: GATEDRIVE; Value: 1
bitfield16 | EnableBits |  |  | Name: REBUS_CONNECT; Value: 2
bitfield16 | EnableBits |  |  | Name: BATT_CONNECT; Value: 3
bitfield16 | EnableBits |  |  | Name: INT_FAN; Value: 4
bitfield16 | EnableBits |  |  | Name: EXT_FAN; Value: 5
bitfield16 | EnableBits |  |  | Name: FAN_OVERRIDE; Value: 6
bitfield16 | EnableBits |  |  | Name: BLKSTART_BATT_CHG; Value: 7
bitfield16 | EnableBits |  |  | Name: CONV1; Value: 8
bitfield16 | EnableBits |  |  | Name: CONV2; Value: 9
bitfield16 | EnableBits |  |  | Name: AUTOMODE; Value: 10
bitfield16 | EnableBits |  |  | Name: 120HZ_FILTER; Value: 11
bitfield16 | EnableBits |  |  | Name: BMS; Value: 12
bitfield16 | EnableBits |  |  | Name: INHIBIT_CSZ; Value: 13
bitfield16 | EnableBits |  |  | Name: CSZERO; Value: 14
bitfield16 | EnableBits |  |  | Name: USB_RCP; Value: 15
bitfield16 | InhibitBits |  |  | Name: PRECHARGE_FAIL; Value: 0
bitfield16 | InhibitBits |  |  | Name: IBAT_INTEGRAL; Value: 1
bitfield16 | InhibitBits |  |  | Name: NO_REBUS_ENABLES; Value: 2
bitfield16 | InhibitBits |  |  | Name: BATTERY_BMS; Value: 3
bitfield16 | InhibitBits |  |  | Name: VBUS_OV; Value: 4
bitfield16 | InhibitBits |  |  | Name: VDC_OV; Value: 5
bitfield16 | InhibitBits |  |  | Name: VBAT_OV; Value: 6
bitfield16 | InhibitBits |  |  | Name: IBAT_OV; Value: 7
bitfield16 | InhibitBits |  |  | Name: NO_INPUT; Value: 8
bitfield16 | InhibitBits |  |  | Name: BATT_VERYLOW_TIMEOUT; Value: 9
bitfield16 | InhibitBits |  |  | Name: BATT_CRIT_LOW; Value: 10
bitfield16 | InhibitBits |  |  | Name: BATT_CRIT_HIGH; Value: 11
bitfield16 | InhibitBits |  |  | Name: UNUSED12; Value: 12
bitfield16 | InhibitBits |  |  | Name: UNUSED13; Value: 13
bitfield16 | InhibitBits |  |  | Name: UNUSED14; Value: 14
bitfield16 | InhibitBits |  |  | Name: UNUSED15; Value: 15
bitfield16 | StatusBits |  |  | Name: DEADMAN_UP; Value: 0
bitfield16 | StatusBits |  |  | Name: REBUS_PRECHARGING; Value: 1
bitfield16 | StatusBits |  |  | Name: REBUS_CONNECTED; Value: 2
bitfield16 | StatusBits |  |  | Name: BATT_CONNECTED; Value: 3
bitfield16 | StatusBits |  |  | Name: CHARGING; Value: 4
bitfield16 | StatusBits |  |  | Name: DISCHARGING; Value: 5
bitfield16 | StatusBits |  |  | Name: COULD_CHARGE; Value: 6
bitfield16 | StatusBits |  |  | Name: COULD_DISCHARGE; Value: 7
bitfield16 | StatusBits |  |  | Name: UNUSED8; Value: 8
bitfield16 | StatusBits |  |  | Name: UNUSED9; Value: 9
bitfield16 | StatusBits |  |  | Name: UNUSED10; Value: 10
bitfield16 | StatusBits |  |  | Name: UNUSED11; Value: 11
bitfield16 | StatusBits |  |  | Name: GFD_READY; Value: 12
bitfield16 | StatusBits |  |  | Name: PLM_READY; Value: 13
bitfield16 | StatusBits |  |  | Name: UNUSED14; Value: 14
bitfield16 | StatusBits |  |  | Name: UNUSED15; Value: 15
bitfield16 | BMSStatus |  |  | Name: ENABLE_DISCHARGE; Value: 0
bitfield16 | BMSStatus |  |  | Name: LOW_SOC; Value: 1
bitfield16 | BMSStatus |  |  | Name: VERYLOW_SOC; Value: 2
bitfield16 | BMSStatus |  |  | Name: CRITLOW_SOC; Value: 3
bitfield16 | BMSStatus |  |  | Name: ENABLE_CHARGE; Value: 4
bitfield16 | BMSStatus |  |  | Name: HIGH_SOC; Value: 5
bitfield16 | BMSStatus |  |  | Name: VERYHIGH_SOC; Value: 6
bitfield16 | BMSStatus |  |  | Name: CRITHIGH_SOC; Value: 7
bitfield16 | BMSStatus |  |  | Name: BMS_UP; Value: 8
bitfield16 | BMSStatus |  |  | Name: COMM_OK; Value: 9
bitfield16 | BMSStatus |  |  | Name: BATT_READY; Value: 10
bitfield16 | BMSStatus |  |  | Name: UNUSED; Value: 11
bitfield16 | BMSStatus |  |  | Name: CHARGE_WARNING; Value: 12
bitfield16 | BMSStatus |  |  | Name: DISCHARGE_WARNING; Value: 13
bitfield16 | BMSStatus |  |  | Name: UNUSED14; Value: 14
bitfield16 | BMSStatus |  |  | Name: FLOAT; Value: 15

## 64252
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Panasonic DCB105 Module Warranty Data | 64252 | uint16 |  |  | R | M | Data from DCB105 modules required for Panasonic warranty
Header |  | 1 |  | 1 | L |  | 16 + (RB Count * 16) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | Size: 1; Name: sf_10; Type: sunssf; R/W: R | M
Fixed Block |  | 3 | 1 | Size: 1; Name: sf_100; Type: sunssf; R/W: R | M
Fixed Block |  | 4 | 2 | Size: 1; Name: sf_1000; Type: sunssf; R/W: R | M
Fixed Block |  | 5 | 3 | 1 | NMod | Module Count |  | uint16 |  |  | R | M | Number of DCB modules that the system is configured for
Fixed Block |  | 6 | 4 | 2 | WhIn | WhIn |  | int32 | Wh |  | R | M | Cummulative energy into battery string
Fixed Block |  | 8 | 6 | 2 | WhOut | WhOut |  | int32 | Wh |  | R | M | Cummulative energy out of battery string
Fixed Block |  | 10 | 8 | 2 | AhIn | AhIn |  | int32 | Ah |  | R | M | Cummulative charge into battery string
Fixed Block |  | 12 | 10 | 2 | AhOut | AhOut |  | int32 | Ah |  | R | M | Cummulative charge out of battery string
Fixed Block |  | 14 | 12 | 1 | THSin | Heat Sink Temp |  | int16 | C | sf_10 | R | M | Temperature of heat sink input
Fixed Block |  | 15 | 13 | 1 | W | Power |  | int16 | W |  | R | M | Battery power right now
Fixed Block |  | 16 | 14 | 1 | I | Current |  | int16 | A | sf_100 | R | M | Instantaneous current measurement | Because the modules are in series, the current is the same through all modules.
Fixed Block |  | 17 | 15 | 1 | V | String Voltage |  | int16 | V | sf_10 | R | M | Voltage of whole string of batteries
Repeating Block |  | 18 | 0 | 1 | SN | Serial Number |  | uint16 |  |  | R | M | Serial Number
Repeating Block |  | 19 | 1 | 1 | ManDt | Product Date Code |  | uint16 |  |  | R | M | Manufacture date
Repeating Block |  | 20 | 2 | 1 | ProgVer | Program Version |  | uint16 |  |  | R | M | Program version
Repeating Block |  | 21 | 3 | 1 | DataVer | Data Version |  | uint16 |  |  | R | M | Data version
Repeating Block |  | 22 | 4 | 1 | StatusFlags | Status Flags |  | bitfield16 |  |  | R | M | Status
Repeating Block |  | 23 | 5 | 1 | WarningFlags | Warning Flags |  | bitfield16 |  |  | R | M | Warnings
Repeating Block |  | 24 | 6 | 1 | AlarmFlags | Alarm Flags |  | bitfield16 |  |  | R | M | Alarms
Repeating Block |  | 25 | 7 | 1 | ErrorFlags | Error Flags |  | bitfield16 |  |  | R | M | Errors
Repeating Block |  | 26 | 8 | 1 | ModuleIOFlags | Module IO Flags |  | bitfield16 |  |  | R | M | IO flags
Repeating Block |  | 27 | 9 | 1 | SOC | State of Charge |  | uint16 |  | sf_10 | R | M | State of Charge
Repeating Block |  | 28 | 10 | 1 | SOH | State of Health |  | uint16 |  | sf_10 | R | M | State of Health
Repeating Block |  | 29 | 11 | 1 | MaxCellV | MaxCellV |  | uint16 | V | sf_1000 | R | M | Maximum cell voltage
Repeating Block |  | 30 | 12 | 1 | MinCellV | MinCellV |  | uint16 | V | sf_1000 | R | M | Minimum cell voltage
Repeating Block |  | 31 | 13 | 1 | PackV | PackV |  | uint16 | V | sf_100 | R | M | Module voltage
Repeating Block |  | 32 | 14 | 1 | MaxCellT | MaxCellT |  | int16 | C | sf_10 | R | M | Maximum cell temperature
Repeating Block |  | 33 | 15 | 1 | MinCellT | MinCellT |  | int16 | C | sf_10 | R | M | Minimum cell temperature