## Info
Date | 2018-06-27 11:25:28
Manufacturer Name | Pika Energy
Product Name | Beacon
Product Models
Product Description | Communications Gateway

## 1
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40002 | ID |  |  | 1
40003 | L |  |  | 66
40004 | Manufacturer (Mn) |  |  | Pika | R
40020 | Model (Md) |  |  | REbus Beacon | R
40036 | Options (Opt) |  |  | unimplemented | R
40044 | Version (Vr) |  |  | 100_11200 | R
40052 | Serial Number (SN) |  |  | 00010012000E | R
40068 | Device Address (DA) |  |  | unimplemented | RW
40069 | Pad |  |  |  | R

## 64250
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40070 | ID |  |  | 64250
40071 | L |  |  | 220
40072 | Owner's First Name (FNm) |  |  | supported | RW
40088 | Owner's Last Name (LNm) |  |  | supported | RW
40104 | Owner's Email (Em) |  |  | supported | RW
40124 | Address Line 1 (Adr1) |  |  | supported | RW
40144 | Address Line 2 (Adr2) |  |  | unimplemented | RW
40164 | City (Cty) |  |  | supported | RW
40180 | State/Province (St) |  |  | supported | RW
40196 | Zip/Postal Code (Zp) |  |  | supported | RW
40204 | Country (Cntr) |  |  | supported | RW
40220 | Phone (Phn) |  |  | supported | RW
40228 | Installer's first name (IFNm) |  |  | supported | RW
40244 | Installer's last name (ILNm) |  |  | supported | RW
40260 | Installer's email (IEm) |  |  | supported | RW
40276 | Installer Company (ICo) |  |  | supported | RW
40284 | Installer's phone (IPhn) |  |  | supported | RW

## 16
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40292 | ID |  |  | 16
40293 | L |  |  | 52
40294 | Name (Nam) |  |  | supported | RW
40298 | Config (Cfg) |  |  | supported | RW
|  |  | static (STATIC) | supported
|  |  | DHCP | supported
40299 | Control (Ctl) |  |  | unimplemented | RW
|  |  | DNS (ENABLE_DNS) | supported
|  |  | NTP (ENABLE_NTP) | supported
40300 | Address (Addr) |  |  | supported | RW
40308 | Netmask (Msk) |  |  | supported | RW
40316 | Gateway (Gw) |  |  | supported | RW
40324 | DNS1 |  |  | supported | RW
40332 | DNS2 |  |  | supported | RW
40340 | MAC |  |  | supported | R
40344 | Link Control (LnkCtl) |  |  | unimplemented | RW
|  |  | auto-negotiate (AUTONEGOTIATE) | supported
|  |  | full duplex (FULL_DUPLEX) | supported
|  |  | 10Mbs (FORCE_10MB) | supported
|  |  | 100Mbs (FORCE_100MB) | supported
|  |  | 1Gbs (FORCE_1GB) | supported
40345 | Pad |  |  |  | R

## 133
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40346 | ID |  |  | 133
40347 | L |  |  | 486
40348 | ActSchd |  |  | supported | RW
|  |  | SCHED1 | supported
|  |  | SCHED2 | supported
|  |  | SCHED3 | supported
|  |  | SCHED4 | supported
|  |  | SCHED5 | supported
|  |  | SCHED6 | supported
|  |  | SCHED7 | supported
|  |  | SCHED8 | supported
|  |  | SCHED9 | supported
|  |  | SCHED10 | supported
|  |  | SCHED11 | supported
|  |  | SCHED12 | supported
|  |  | SCHED13 | supported
|  |  | SCHED14 | supported
|  |  | SCHED15 | supported
|  |  | SCHED16 | supported
|  |  | SCHED17 | supported
|  |  | SCHED18 | supported
|  |  | SCHED19 | supported
|  |  | SCHED20 | supported
|  |  | SCHED21 | supported
|  |  | SCHED22 | supported
|  |  | SCHED23 | supported
|  |  | SCHED24 | supported
|  |  | SCHED25 | supported
|  |  | SCHED26 | supported
|  |  | SCHED27 | supported
|  |  | SCHED28 | supported
|  |  | SCHED29 | supported
|  |  | SCHED30 | supported
|  |  | SCHED31 | supported
|  |  | SCHED32 | supported
40350 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40351 | NSchd |  |  | supported | R
40352 | NPts |  |  | supported | R
40353 | Pad |  |  |  | R
40354 | ActPts | 1 |  | supported | RW
40355 | StrTms | 1 |  | supported | RW
40357 | RepPer | 1 |  | supported | RW
40358 | SchdTyp (IntvTyp) | 1 |  | supported | RW
|  |  | ONETIME | supported
|  |  | DAILY | supported
|  |  | WEEKLY | supported
|  |  | MONTHLY | supported
|  |  | WEEKDAY | supported
|  |  | HOLIDAY | supported
|  |  | WEEKEND | supported
|  |  | YEARLY | supported
40359 | XTyp | 1 |  | supported | RW
|  |  | UNSET | supported
|  |  | TIME | supported
|  |  | TEMP | supported
|  |  | PRICE | supported
|  |  | OTHER | supported
40360 | X_SF | 1 |  | 0 | RW
40361 | YTyp | 1 |  | supported | RW
|  |  | UNSET | supported
|  |  | WMax | supported
|  |  | RSRVD2 | supported
|  |  | PF | supported
|  |  | RSRVD4 | supported
|  |  | WATT_PRICE | supported
|  |  | VAR_PRICE | supported
|  |  | RSRVD7 | supported
|  |  | VOLT_VAR_ARRAY | supported
|  |  | WChaGra | supported
|  |  | WDisChaGra | supported
|  |  | VArAval | supported
|  |  | Schedule | supported
|  |  | OTHER | supported
40362 | Y_SF | 1 |  | 0 | RW
40363 | X1 | 1 |  | supported | RW
40365 | Y1 | 1 |  | supported | RW
40367 | X2 | 1 |  | supported | RW
40369 | Y2 | 1 |  | supported | RW
40371 | X3 | 1 |  | supported | RW
40373 | Y3 | 1 |  | supported | RW
40375 | X4 | 1 |  | supported | RW
40377 | Y4 | 1 |  | supported | RW
40379 | X5 | 1 |  | supported | RW
40381 | Y5 | 1 |  | supported | RW
40383 | X6 | 1 |  | supported | RW
40385 | Y6 | 1 |  | supported | RW
40387 | X7 | 1 |  | supported | RW
40389 | Y7 | 1 |  | supported | RW
40391 | X8 | 1 |  | supported | RW
40393 | Y8 | 1 |  | supported | RW
40395 | X9 | 1 |  | supported | RW
40397 | Y9 | 1 |  | supported | RW
40399 | X10 | 1 |  | supported | RW
40401 | Y10 | 1 |  | supported | RW
40403 | Nam | 1 |  | supported | RW
40411 | WinTms | 1 |  | supported | RW
40412 | RmpTms | 1 |  | supported | RW
40413 | ActIndx | 1 |  | supported | R
40414 | ActPts | 2 |  | supported | RW
40415 | StrTms | 2 |  | supported | RW
40417 | RepPer | 2 |  | supported | RW
40418 | SchdTyp (IntvTyp) | 2 |  | supported | RW
40419 | XTyp | 2 |  | supported | RW
40420 | X_SF | 2 |  | 0 | RW
40421 | YTyp | 2 |  | supported | RW
40422 | Y_SF | 2 |  | 0 | RW
40423 | X1 | 2 |  | supported | RW
40425 | Y1 | 2 |  | supported | RW
40427 | X2 | 2 |  | supported | RW
40429 | Y2 | 2 |  | supported | RW
40431 | X3 | 2 |  | supported | RW
40433 | Y3 | 2 |  | supported | RW
40435 | X4 | 2 |  | supported | RW
40437 | Y4 | 2 |  | supported | RW
40439 | X5 | 2 |  | supported | RW
40441 | Y5 | 2 |  | supported | RW
40443 | X6 | 2 |  | supported | RW
40445 | Y6 | 2 |  | supported | RW
40447 | X7 | 2 |  | supported | RW
40449 | Y7 | 2 |  | supported | RW
40451 | X8 | 2 |  | supported | RW
40453 | Y8 | 2 |  | supported | RW
40455 | X9 | 2 |  | supported | RW
40457 | Y9 | 2 |  | supported | RW
40459 | X10 | 2 |  | supported | RW
40461 | Y10 | 2 |  | supported | RW
40463 | Nam | 2 |  | supported | RW
40471 | WinTms | 2 |  | supported | RW
40472 | RmpTms | 2 |  | supported | RW
40473 | ActIndx | 2 |  | supported | R
40474 | ActPts | 3 |  | supported | RW
40475 | StrTms | 3 |  | supported | RW
40477 | RepPer | 3 |  | supported | RW
40478 | SchdTyp (IntvTyp) | 3 |  | supported | RW
40479 | XTyp | 3 |  | supported | RW
40480 | X_SF | 3 |  | 0 | RW
40481 | YTyp | 3 |  | supported | RW
40482 | Y_SF | 3 |  | 0 | RW
40483 | X1 | 3 |  | supported | RW
40485 | Y1 | 3 |  | supported | RW
40487 | X2 | 3 |  | supported | RW
40489 | Y2 | 3 |  | supported | RW
40491 | X3 | 3 |  | supported | RW
40493 | Y3 | 3 |  | supported | RW
40495 | X4 | 3 |  | supported | RW
40497 | Y4 | 3 |  | supported | RW
40499 | X5 | 3 |  | supported | RW
40501 | Y5 | 3 |  | supported | RW
40503 | X6 | 3 |  | supported | RW
40505 | Y6 | 3 |  | supported | RW
40507 | X7 | 3 |  | supported | RW
40509 | Y7 | 3 |  | supported | RW
40511 | X8 | 3 |  | supported | RW
40513 | Y8 | 3 |  | supported | RW
40515 | X9 | 3 |  | supported | RW
40517 | Y9 | 3 |  | supported | RW
40519 | X10 | 3 |  | supported | RW
40521 | Y10 | 3 |  | supported | RW
40523 | Nam | 3 |  | supported | RW
40531 | WinTms | 3 |  | supported | RW
40532 | RmpTms | 3 |  | supported | RW
40533 | ActIndx | 3 |  | supported | R
40534 | ActPts | 4 |  | supported | RW
40535 | StrTms | 4 |  | supported | RW
40537 | RepPer | 4 |  | supported | RW
40538 | SchdTyp (IntvTyp) | 4 |  | supported | RW
40539 | XTyp | 4 |  | supported | RW
40540 | X_SF | 4 |  | 0 | RW
40541 | YTyp | 4 |  | supported | RW
40542 | Y_SF | 4 |  | 0 | RW
40543 | X1 | 4 |  | supported | RW
40545 | Y1 | 4 |  | supported | RW
40547 | X2 | 4 |  | supported | RW
40549 | Y2 | 4 |  | supported | RW
40551 | X3 | 4 |  | supported | RW
40553 | Y3 | 4 |  | supported | RW
40555 | X4 | 4 |  | supported | RW
40557 | Y4 | 4 |  | supported | RW
40559 | X5 | 4 |  | supported | RW
40561 | Y5 | 4 |  | supported | RW
40563 | X6 | 4 |  | supported | RW
40565 | Y6 | 4 |  | supported | RW
40567 | X7 | 4 |  | supported | RW
40569 | Y7 | 4 |  | supported | RW
40571 | X8 | 4 |  | supported | RW
40573 | Y8 | 4 |  | supported | RW
40575 | X9 | 4 |  | supported | RW
40577 | Y9 | 4 |  | supported | RW
40579 | X10 | 4 |  | supported | RW
40581 | Y10 | 4 |  | supported | RW
40583 | Nam | 4 |  | supported | RW
40591 | WinTms | 4 |  | supported | RW
40592 | RmpTms | 4 |  | supported | RW
40593 | ActIndx | 4 |  | supported | R
40594 | ActPts | 5 |  | supported | RW
40595 | StrTms | 5 |  | supported | RW
40597 | RepPer | 5 |  | supported | RW
40598 | SchdTyp (IntvTyp) | 5 |  | supported | RW
40599 | XTyp | 5 |  | supported | RW
40600 | X_SF | 5 |  | 0 | RW
40601 | YTyp | 5 |  | supported | RW
40602 | Y_SF | 5 |  | 0 | RW
40603 | X1 | 5 |  | supported | RW
40605 | Y1 | 5 |  | supported | RW
40607 | X2 | 5 |  | supported | RW
40609 | Y2 | 5 |  | supported | RW
40611 | X3 | 5 |  | supported | RW
40613 | Y3 | 5 |  | supported | RW
40615 | X4 | 5 |  | supported | RW
40617 | Y4 | 5 |  | supported | RW
40619 | X5 | 5 |  | supported | RW
40621 | Y5 | 5 |  | supported | RW
40623 | X6 | 5 |  | supported | RW
40625 | Y6 | 5 |  | supported | RW
40627 | X7 | 5 |  | supported | RW
40629 | Y7 | 5 |  | supported | RW
40631 | X8 | 5 |  | supported | RW
40633 | Y8 | 5 |  | supported | RW
40635 | X9 | 5 |  | supported | RW
40637 | Y9 | 5 |  | supported | RW
40639 | X10 | 5 |  | supported | RW
40641 | Y10 | 5 |  | supported | RW
40643 | Nam | 5 |  | supported | RW
40651 | WinTms | 5 |  | supported | RW
40652 | RmpTms | 5 |  | supported | RW
40653 | ActIndx | 5 |  | supported | R
40654 | ActPts | 6 |  | supported | RW
40655 | StrTms | 6 |  | supported | RW
40657 | RepPer | 6 |  | supported | RW
40658 | SchdTyp (IntvTyp) | 6 |  | supported | RW
40659 | XTyp | 6 |  | supported | RW
40660 | X_SF | 6 |  | 0 | RW
40661 | YTyp | 6 |  | supported | RW
40662 | Y_SF | 6 |  | 0 | RW
40663 | X1 | 6 |  | supported | RW
40665 | Y1 | 6 |  | supported | RW
40667 | X2 | 6 |  | supported | RW
40669 | Y2 | 6 |  | supported | RW
40671 | X3 | 6 |  | supported | RW
40673 | Y3 | 6 |  | supported | RW
40675 | X4 | 6 |  | supported | RW
40677 | Y4 | 6 |  | supported | RW
40679 | X5 | 6 |  | supported | RW
40681 | Y5 | 6 |  | supported | RW
40683 | X6 | 6 |  | supported | RW
40685 | Y6 | 6 |  | supported | RW
40687 | X7 | 6 |  | supported | RW
40689 | Y7 | 6 |  | supported | RW
40691 | X8 | 6 |  | supported | RW
40693 | Y8 | 6 |  | supported | RW
40695 | X9 | 6 |  | supported | RW
40697 | Y9 | 6 |  | supported | RW
40699 | X10 | 6 |  | supported | RW
40701 | Y10 | 6 |  | supported | RW
40703 | Nam | 6 |  | supported | RW
40711 | WinTms | 6 |  | supported | RW
40712 | RmpTms | 6 |  | supported | RW
40713 | ActIndx | 6 |  | supported | R
40714 | ActPts | 7 |  | supported | RW
40715 | StrTms | 7 |  | supported | RW
40717 | RepPer | 7 |  | supported | RW
40718 | SchdTyp (IntvTyp) | 7 |  | supported | RW
40719 | XTyp | 7 |  | supported | RW
40720 | X_SF | 7 |  | 0 | RW
40721 | YTyp | 7 |  | supported | RW
40722 | Y_SF | 7 |  | 0 | RW
40723 | X1 | 7 |  | supported | RW
40725 | Y1 | 7 |  | supported | RW
40727 | X2 | 7 |  | supported | RW
40729 | Y2 | 7 |  | supported | RW
40731 | X3 | 7 |  | supported | RW
40733 | Y3 | 7 |  | supported | RW
40735 | X4 | 7 |  | supported | RW
40737 | Y4 | 7 |  | supported | RW
40739 | X5 | 7 |  | supported | RW
40741 | Y5 | 7 |  | supported | RW
40743 | X6 | 7 |  | supported | RW
40745 | Y6 | 7 |  | supported | RW
40747 | X7 | 7 |  | supported | RW
40749 | Y7 | 7 |  | supported | RW
40751 | X8 | 7 |  | supported | RW
40753 | Y8 | 7 |  | supported | RW
40755 | X9 | 7 |  | supported | RW
40757 | Y9 | 7 |  | supported | RW
40759 | X10 | 7 |  | supported | RW
40761 | Y10 | 7 |  | supported | RW
40763 | Nam | 7 |  | supported | RW
40771 | WinTms | 7 |  | supported | RW
40772 | RmpTms | 7 |  | supported | RW
40773 | ActIndx | 7 |  | supported | R
40774 | ActPts | 8 |  | supported | RW
40775 | StrTms | 8 |  | supported | RW
40777 | RepPer | 8 |  | supported | RW
40778 | SchdTyp (IntvTyp) | 8 |  | supported | RW
40779 | XTyp | 8 |  | supported | RW
40780 | X_SF | 8 |  | 0 | RW
40781 | YTyp | 8 |  | supported | RW
40782 | Y_SF | 8 |  | 0 | RW
40783 | X1 | 8 |  | supported | RW
40785 | Y1 | 8 |  | supported | RW
40787 | X2 | 8 |  | supported | RW
40789 | Y2 | 8 |  | supported | RW
40791 | X3 | 8 |  | supported | RW
40793 | Y3 | 8 |  | supported | RW
40795 | X4 | 8 |  | supported | RW
40797 | Y4 | 8 |  | supported | RW
40799 | X5 | 8 |  | supported | RW
40801 | Y5 | 8 |  | supported | RW
40803 | X6 | 8 |  | supported | RW
40805 | Y6 | 8 |  | supported | RW
40807 | X7 | 8 |  | supported | RW
40809 | Y7 | 8 |  | supported | RW
40811 | X8 | 8 |  | supported | RW
40813 | Y8 | 8 |  | supported | RW
40815 | X9 | 8 |  | supported | RW
40817 | Y9 | 8 |  | supported | RW
40819 | X10 | 8 |  | supported | RW
40821 | Y10 | 8 |  | supported | RW
40823 | Nam | 8 |  | supported | RW
40831 | WinTms | 8 |  | supported | RW
40832 | RmpTms | 8 |  | supported | RW
40833 | ActIndx | 8 |  | supported | R

## 64200
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40834 | ID |  |  | 64200
40835 | L |  |  | 136
40836 | Update number (UpdtN) |  |  | supported | R
40837 | Device count (Ct) |  |  | supported | R
40838 | System Operating Mode (SysMd) |  |  | supported | RW
|  |  | SAFETY_SHUTDOWN | supported
|  |  | GRID_CONNECT | supported
|  |  | SELF_SUPPLY | supported
|  |  | CLEAN_BACKUP | supported
|  |  | PRIORITY_BACKUP | supported
|  |  | ARBITRAGE | supported
|  |  | FULL_EXPORT | supported
40839 | VT_sf |  |  | -1 | R
40840 | I_sf |  |  | -2 | R
40841 | Current system time (Time) |  |  | supported | R
40843 | Clear device list (Clr) |  |  | supported | RW
|  |  | NO | supported
|  |  | CLEAR | supported
40844 | Manufacturer (Man) | 1 |  | supported | R
|  |  | PIKA_ENERGY | supported
40845 | Device Type (Dev) | 1 |  | supported | R
|  |  | PV_LINK | supported
|  |  | INVERTER | supported
|  |  | BATTERY | supported
40846 | Device ID (ID) | 1 |  | supported | R
40847 | Enable (Ena) | 1 |  | supported | RW
|  |  | disabled (DISABLED) | supported
|  |  | ENABLED | supported
40848 | ModBus ID (UnitID) | 1 |  | supported | R
40849 | Update Time (UpdtTm) | 1 |  | supported | R
40851 | State (St) | 1 |  | supported | R
|  |  | device offline (UNKNOWN) | supported
|  |  | disabled (DISABLED) | supported
|  |  | initializing (INITIALIZING) | supported
|  |  | powering up (POWERING_UP) | supported
|  |  | connecting to REbus (CONNECTING_BUS) | supported
|  |  | disconnecting REbus (DISCONNECTING_BUS) | supported
|  |  | testing REbus... (TESTING_BUS) | supported
|  |  | low REbus voltage (LOW_BUS_VOLTAGE) | supported
|  |  | standby (STANDBY) | supported
|  |  | waiting (WAITING) | supported
|  |  | waiting - no input (WAITING_NO_INPUT) | supported
|  |  | connecting grid (CONNECTING_GRID) | supported
|  |  | disconnecting grid (DISCONNECTING_GRID) | supported
|  |  | grid connected (GRID_CONNECTED) | supported
|  |  | islanded (ISLANDED) | supported
|  |  | connecting generator (CONNECTING_GENERATOR) | supported
|  |  | generator parallel (GENERATOR_PARALLEL) | supported
|  |  | low input voltage (LOW_INPUT_VOLTAGE) | supported
|  |  | testing input... (TESTING_DEVICE_INPUT) | supported
|  |  | connecting input (CONNECTING_INPUT) | supported
|  |  | disconnecting input (DISCONNECTING_INPUT) | supported
|  |  | calibrating (CALIBRATING) | supported
|  |  | calibration success! (CALIBRATION_SUCCESS) | supported
|  |  | calibration required (CALIBRATION_NEEDED) | supported
|  |  | burning in (BURN_IN) | supported
|  |  | burn in done (BURN_IN_DONE) | supported
|  |  | running, overridden (SCHEDULER_OVERRIDDEN) | supported
|  |  | scheduler disabled (SCHEDULER_DISABLED) | supported
|  |  | running (RUNNING) | supported
|  |  | making power (MAKING_POWER) | supported
|  |  | limiting power (LIMITING_POWER) | supported
|  |  | low wind (LOW_WIND) | supported
|  |  | high wind (HIGH_WIND) | supported
|  |  | low sun (LOW_SUN) | supported
|  |  | charging (CHARGING_BATTERY) | supported
|  |  | float charging (FLOAT_CHARGING_BATTERY) | supported
|  |  | bulk charging (BULK_CHARGING_BATTERY) | supported
|  |  | absorption charging (ABSORPTION_CHARGING_BATTERY) | supported
|  |  | equalizing (EQUALIZE_CHARGING_BATTERY) | supported
|  |  | discharging (DISCHARGING_BATTERY) | supported
|  |  | low battery voltage (LOW_BATTERY_VOLTAGE) | supported
|  |  | error (ERROR_GENERIC) | supported
|  |  | over voltage input (OVER_VOLTAGE_INPUT) | supported
|  |  | over voltage output (OVER_VOLTAGE_OUTPUT) | supported
|  |  | over current input (OVER_CURRENT_INPUT) | supported
|  |  | over current output (OVER_CURRENT_OUTPUT) | supported
|  |  | error: low batt volts (ERROR_LOW_BATTERY_VOLTAGE) | supported
|  |  | over temperature (OVER_TEMPERATURE) | supported
|  |  | err: ground fault (GROUND_FAULT) | supported
|  |  | err: insulation fault (INSULATION_FAULT) | supported
|  |  | calibration mode (CALIBRATION_0) | supported
|  |  | calibration 1 (CALIBRATION_1) | supported
|  |  | calibration 2 (CALIBRATION_2) | supported
|  |  | calibration 3 (CALIBRATION_3) | supported
40852 | REbus Power (P) | 1 |  | supported | R
40853 | Accumulated Energy (E) | 1 |  | supported | R
40855 | REbus Bits (Rb) | 1 |  | supported | R
40856 | REbus Voltage (V) | 1 |  | supported | R
40857 | REbus Current (I) | 1 |  | supported | R
40858 | Device Temperature (T) | 1 |  | supported | R
40859 | Otherdata 0 (O0) | 1 |  | supported | R
40860 | Otherdata 1 (O1) | 1 |  | supported | R
40861 | Otherdata 2 (O2) | 1 |  | supported | R
40862 | Otherdata 3 (O3) | 1 |  | supported | R
40863 | Otherdata 4 (O4) | 1 |  | supported | R
40864 | Otherdata 5 (O5) | 1 |  | supported | R
40865 | Otherdata 6 (O6) | 1 |  | supported | R
40866 | Otherdata 7 (O7) | 1 |  | supported | R
40867 | Otherdata 8 (O8) | 1 |  | supported | R
40868 | Otherdata 9 (O9) | 1 |  | supported | R
40869 | Otherdata A (OA) | 1 |  | supported | R
40870 | Otherdata B (OB) | 1 |  | supported | R
40871 | Otherdata C (OC) | 1 |  | supported | R
40872 | Otherdata D (OD) | 1 |  | supported | R
40873 | Otherdata E (OE) | 1 |  | supported | R
40874 | Otherdata F (OF) | 1 |  | supported | R
40875 | Otherdata G (OG) | 1 |  | supported | R
40876 | Manufacturer (Man) | 2 |  | supported | R
40877 | Device Type (Dev) | 2 |  | supported | R
40878 | Device ID (ID) | 2 |  | supported | R
40879 | Enable (Ena) | 2 |  | supported | RW
40880 | ModBus ID (UnitID) | 2 |  | supported | R
40881 | Update Time (UpdtTm) | 2 |  | supported | R
40883 | State (St) | 2 |  | supported | R
40884 | REbus Power (P) | 2 |  | supported | R
40885 | Accumulated Energy (E) | 2 |  | supported | R
40887 | REbus Bits (Rb) | 2 |  | supported | R
40888 | REbus Voltage (V) | 2 |  | supported | R
40889 | REbus Current (I) | 2 |  | supported | R
40890 | Device Temperature (T) | 2 |  | supported | R
40891 | Otherdata 0 (O0) | 2 |  | supported | R
40892 | Otherdata 1 (O1) | 2 |  | supported | R
40893 | Otherdata 2 (O2) | 2 |  | supported | R
40894 | Otherdata 3 (O3) | 2 |  | supported | R
40895 | Otherdata 4 (O4) | 2 |  | supported | R
40896 | Otherdata 5 (O5) | 2 |  | supported | R
40897 | Otherdata 6 (O6) | 2 |  | supported | R
40898 | Otherdata 7 (O7) | 2 |  | supported | R
40899 | Otherdata 8 (O8) | 2 |  | supported | R
40900 | Otherdata 9 (O9) | 2 |  | supported | R
40901 | Otherdata A (OA) | 2 |  | supported | R
40902 | Otherdata B (OB) | 2 |  | supported | R
40903 | Otherdata C (OC) | 2 |  | supported | R
40904 | Otherdata D (OD) | 2 |  | supported | R
40905 | Otherdata E (OE) | 2 |  | supported | R
40906 | Otherdata F (OF) | 2 |  | supported | R
40907 | Otherdata G (OG) | 2 |  | supported | R
40908 | Manufacturer (Man) | 3 |  | supported | R
40909 | Device Type (Dev) | 3 |  | supported | R
40910 | Device ID (ID) | 3 |  | supported | R
40911 | Enable (Ena) | 3 |  | supported | RW
40912 | ModBus ID (UnitID) | 3 |  | supported | R
40913 | Update Time (UpdtTm) | 3 |  | supported | R
40915 | State (St) | 3 |  | supported | R
40916 | REbus Power (P) | 3 |  | supported | R
40917 | Accumulated Energy (E) | 3 |  | supported | R
40919 | REbus Bits (Rb) | 3 |  | supported | R
40920 | REbus Voltage (V) | 3 |  | supported | R
40921 | REbus Current (I) | 3 |  | supported | R
40922 | Device Temperature (T) | 3 |  | supported | R
40923 | Otherdata 0 (O0) | 3 |  | supported | R
40924 | Otherdata 1 (O1) | 3 |  | supported | R
40925 | Otherdata 2 (O2) | 3 |  | supported | R
40926 | Otherdata 3 (O3) | 3 |  | supported | R
40927 | Otherdata 4 (O4) | 3 |  | supported | R
40928 | Otherdata 5 (O5) | 3 |  | supported | R
40929 | Otherdata 6 (O6) | 3 |  | supported | R
40930 | Otherdata 7 (O7) | 3 |  | supported | R
40931 | Otherdata 8 (O8) | 3 |  | supported | R
40932 | Otherdata 9 (O9) | 3 |  | supported | R
40933 | Otherdata A (OA) | 3 |  | supported | R
40934 | Otherdata B (OB) | 3 |  | supported | R
40935 | Otherdata C (OC) | 3 |  | supported | R
40936 | Otherdata D (OD) | 3 |  | supported | R
40937 | Otherdata E (OE) | 3 |  | supported | R
40938 | Otherdata F (OF) | 3 |  | supported | R
40939 | Otherdata G (OG) | 3 |  | supported | R
40940 | Manufacturer (Man) | 4 |  | supported | R
40941 | Device Type (Dev) | 4 |  | supported | R
40942 | Device ID (ID) | 4 |  | supported | R
40943 | Enable (Ena) | 4 |  | supported | RW
40944 | ModBus ID (UnitID) | 4 |  | supported | R
40945 | Update Time (UpdtTm) | 4 |  | supported | R
40947 | State (St) | 4 |  | supported | R
40948 | REbus Power (P) | 4 |  | supported | R
40949 | Accumulated Energy (E) | 4 |  | supported | R
40951 | REbus Bits (Rb) | 4 |  | supported | R
40952 | REbus Voltage (V) | 4 |  | supported | R
40953 | REbus Current (I) | 4 |  | supported | R
40954 | Device Temperature (T) | 4 |  | supported | R
40955 | Otherdata 0 (O0) | 4 |  | supported | R
40956 | Otherdata 1 (O1) | 4 |  | supported | R
40957 | Otherdata 2 (O2) | 4 |  | supported | R
40958 | Otherdata 3 (O3) | 4 |  | supported | R
40959 | Otherdata 4 (O4) | 4 |  | supported | R
40960 | Otherdata 5 (O5) | 4 |  | supported | R
40961 | Otherdata 6 (O6) | 4 |  | supported | R
40962 | Otherdata 7 (O7) | 4 |  | supported | R
40963 | Otherdata 8 (O8) | 4 |  | supported | R
40964 | Otherdata 9 (O9) | 4 |  | supported | R
40965 | Otherdata A (OA) | 4 |  | supported | R
40966 | Otherdata B (OB) | 4 |  | supported | R
40967 | Otherdata C (OC) | 4 |  | supported | R
40968 | Otherdata D (OD) | 4 |  | supported | R
40969 | Otherdata E (OE) | 4 |  | supported | R
40970 | Otherdata F (OF) | 4 |  | supported | R
40971 | Otherdata G (OG) | 4 |  | supported | R