## Index
Model | Label | Description | Notes
1 | Common | Make, model and serial number information for this device
16 | Simple IP Network Settings | Simple IPv4 network stack configuration
133 | Basic Scheduling | Basic Scheduling | Ref 2: 2.2.8
64200 | REbus Device Directory | Device List | Use this model to to read and change the system operating mode (sysmode), determine which devices are on the REbus system, read device status updates, enable/disable devices, and get each device's Modbus Unit ID.

## 1
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Common | 1 | uint16 |  |  | R | M | Make, model and serial number information for this device
Header |  | 1 |  | 1 | L |  | 66 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 16 | Mn | Manufacturer |  | string |  |  | R | M | Well known value registered with SunSpec for compliance
Fixed Block |  | 18 | 16 | 16 | Md | Model |  | string |  |  | R | M | Manufacturer specific value (32 chars)
Fixed Block |  | 34 | 32 | 8 | Opt | Options |  | string |  |  | R | O | Manufacturer specific value (16 chars)
Fixed Block |  | 42 | 40 | 8 | Vr | Version |  | string |  |  | R | O | Manufacturer specific value (16 chars)
Fixed Block |  | 50 | 48 | 16 | SN | Serial Number |  | string |  |  | R | M | Manufacturer specific value (32 chars)
Fixed Block |  | 66 | 64 | 1 | DA | Device Address |  | uint16 |  |  | RW | O | Modbus device address
Fixed Block |  | 67 | 65 | Size: 1; Name: Pad; Type: pad; R/W: R | O | Force even alignment

## 16
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Simple IP Network Settings | 16 | uint16 |  |  | R | M | Simple IPv4 network stack configuration
Header |  | 1 |  | 1 | L |  | 52 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 4 | Nam | Name |  | string |  |  | RW | O | Interface name. (8 chars)
Fixed Block |  | 6 | 4 | 1 | Cfg | Config |  | enum16 |  |  | RW | M | Enumerated value. Force IPv4 configuration method
Fixed Block |  | 7 | 5 | 1 | Ctl | Control |  | bitfield16 |  |  | RW | M | Bitmask value Configure use of services
Fixed Block |  | 8 | 6 | 8 | Addr | Address |  | string |  |  | RW | M | IP addreess
Fixed Block |  | 16 | 14 | 8 | Msk | Netmask |  | string |  |  | RW | M | Netmask
Fixed Block |  | 24 | 22 | 8 | Gw | Gateway |  | string |  |  | RW | O | Gateway IP address
Fixed Block |  | 32 | 30 | 8 | DNS1 | DNS1 |  | string |  |  | RW | O | 32 bit IP address of DNS server
Fixed Block |  | 40 | 38 | 8 | DNS2 | DNS2 |  | string |  |  | RW | O | 32 bit IP address of DNS server
Fixed Block |  | 48 | 46 | 4 | MAC | MAC |  | eui48 |  |  | R | O | IEEE MAC address of this interface
Fixed Block |  | 52 | 50 | 1 | LnkCtl | Link Control |  | bitfield16 |  |  | RW | O | Bitmask value. Link control flags
Fixed Block |  | 53 | 51 | Size: 1; Name: Pad; Type: pad; R/W: R | O
enum16 | Cfg |  |  | Name: STATIC; Label: static; Value: 0 |  | A static IP address is assigned
enum16 | Cfg |  |  | Name: DHCP; Label: DHCP; Value: 1 |  | Use DHCP to acquire an IP address
bitfield16 | Ctl |  |  | Name: ENABLE_DNS; Label: DNS; Value: 0 |  | Enable DNS use
bitfield16 | Ctl |  |  | Name: ENABLE_NTP; Label: NTP; Value: 1 |  | Enable NTP use
bitfield16 | LnkCtl |  |  | Name: AUTONEGOTIATE; Label: auto-negotiate; Value: 0 |  | Enable auto-negotiation
bitfield16 | LnkCtl |  |  | Name: FULL_DUPLEX; Label: full duplex; Value: 1 |  | Force full duplex operation
bitfield16 | LnkCtl |  |  | Name: FORCE_10MB; Label: 10Mbs; Value: 2 |  | Force 10 Mb/s link speed
bitfield16 | LnkCtl |  |  | Name: FORCE_100MB; Label: 100Mbs; Value: 3 |  | Force 100 Mb/s link speed
bitfield16 | LnkCtl |  |  | Name: FORCE_1GB; Label: 1Gbs; Value: 4 |  | Force 1 Gb/s link speed

## 133
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Basic Scheduling | 133 | uint16 |  |  | R | M | Basic Scheduling | Ref 2: 2.2.8
Header |  | 1 |  | 1 | L |  | 6 + (RB Count * 60) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 2 | ActSchd | ActSchd |  | bitfield32 |  |  | RW | M | Bitfield of active schedules
Fixed Block |  | 4 | 2 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is basic scheduling active.
Fixed Block |  | 5 | 3 | 1 | NSchd | NSchd |  | uint16 |  |  | R | M | Number of schedules supported (recommend min. 4, max 32)
Fixed Block |  | 6 | 4 | 1 | NPts | NPts |  | uint16 |  |  | R | M | Number of schedule entries supuported (maximum of 10).
Fixed Block |  | 7 | 5 | 1 | Pad | Pad |  | pad |  |  | R | O | Pad register.
Repeating Block |  | 8 | 0 | 1 | ActPts | ActPts |  | uint16 |  |  | RW | M | Number of active entries in schedule.
Repeating Block |  | 9 | 1 | 2 | StrTms | StrTms |  | uint32 | Secs |  | RW | M | Schedule start in seconds since 2000 JAN 01 00:00:00 UTC.
Repeating Block |  | 11 | 3 | 1 | RepPer | RepPer |  | uint16 |  |  | RW | M | The repetition count for time-based schedules (0=repeat forever)
Repeating Block |  | 12 | 4 | 1 | IntvTyp | SchdTyp |  | enum16 |  |  | RW | M | The repetition frequency for time-based schedules: no repeat=0
Repeating Block |  | 13 | 5 | 1 | XTyp | XTyp |  | enum16 |  |  | RW | M | The meaning of the X-values in the array.
Repeating Block |  | 14 | 6 | 1 | X_SF | X_SF |  | sunssf |  |  | RW | M | Scale factor for schedule range values.
Repeating Block |  | 15 | 7 | 1 | YTyp | YTyp |  | enum16 |  |  | RW | M | The meaning of the Y-values in the array.
Repeating Block |  | 16 | 8 | 1 | Y_SF | Y_SF |  | sunssf |  |  | RW | M | Scale factor for schedule target values.
Repeating Block |  | 17 | 9 | 2 | X1 | X1 |  | int32 |  | X_SF | RW | M | Entry 1 range.
Repeating Block |  | 19 | 11 | 2 | Y1 | Y1 |  | int32 |  | Y_SF | RW | M | Entry 1 target.
Repeating Block |  | 21 | 13 | 2 | X2 | X2 |  | int32 |  | X_SF | RW | O | Entry 2 range.
Repeating Block |  | 23 | 15 | 2 | Y2 | Y2 |  | int32 |  | Y_SF | RW | O | Entry 2 target.
Repeating Block |  | 25 | 17 | 2 | X3 | X3 |  | int32 |  | X_SF | RW | O | Entry 3 range.
Repeating Block |  | 27 | 19 | 2 | Y3 | Y3 |  | int32 |  | Y_SF | RW | O | Entry 3 target.
Repeating Block |  | 29 | 21 | 2 | X4 | X4 |  | int32 |  | X_SF | RW | O | Entry 4 range.
Repeating Block |  | 31 | 23 | 2 | Y4 | Y4 |  | int32 |  | Y_SF | RW | O | Entry 4 target.
Repeating Block |  | 33 | 25 | 2 | X5 | X5 |  | int32 |  | X_SF | RW | O | Entry 15range.
Repeating Block |  | 35 | 27 | 2 | Y5 | Y5 |  | int32 |  | Y_SF | RW | O | Entry 5 target.
Repeating Block |  | 37 | 29 | 2 | X6 | X6 |  | int32 |  | X_SF | RW | O | Entry 6 range.
Repeating Block |  | 39 | 31 | 2 | Y6 | Y6 |  | int32 |  | Y_SF | RW | O | Entry 6 target.
Repeating Block |  | 41 | 33 | 2 | X7 | X7 |  | int32 |  | X_SF | RW | O | Entry 7 range.
Repeating Block |  | 43 | 35 | 2 | Y7 | Y7 |  | int32 |  | Y_SF | RW | O | Entry 7 target.
Repeating Block |  | 45 | 37 | 2 | X8 | X8 |  | int32 |  | X_SF | RW | O | Entry 8 range.
Repeating Block |  | 47 | 39 | 2 | Y8 | Y8 |  | int32 |  | Y_SF | RW | O | Entry 8 target.
Repeating Block |  | 49 | 41 | 2 | X9 | X9 |  | int32 |  | X_SF | RW | O | Entry 9 range.
Repeating Block |  | 51 | 43 | 2 | Y9 | Y9 |  | int32 |  | Y_SF | RW | O | Entry 9 target.
Repeating Block |  | 53 | 45 | 2 | X10 | X10 |  | int32 |  | X_SF | RW | O | Entry 10 range.
Repeating Block |  | 55 | 47 | 2 | Y10 | Y10 |  | int32 |  | Y_SF | RW | O | Entry 10 target.
Repeating Block |  | 57 | 49 | 8 | Nam | Nam |  | string |  |  | RW | O | Optional description for schedule.
Repeating Block |  | 65 | 57 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for schedule entry change.
Repeating Block |  | 66 | 58 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current target to new target.
Repeating Block |  | 67 | 59 | 1 | ActIndx | ActIndx |  | uint16 |  |  | R | M | Index of active entry in the active schedule.
bitfield32 | ActSchd |  |  | Name: SCHED1; Value: 0
bitfield32 | ActSchd |  |  | Name: SCHED2; Value: 1
bitfield32 | ActSchd |  |  | Name: SCHED3; Value: 2
bitfield32 | ActSchd |  |  | Name: SCHED4; Value: 3
bitfield32 | ActSchd |  |  | Name: SCHED5; Value: 4
bitfield32 | ActSchd |  |  | Name: SCHED6; Value: 5
bitfield32 | ActSchd |  |  | Name: SCHED7; Value: 6
bitfield32 | ActSchd |  |  | Name: SCHED8; Value: 7
bitfield32 | ActSchd |  |  | Name: SCHED9; Value: 8
bitfield32 | ActSchd |  |  | Name: SCHED10; Value: 9
bitfield32 | ActSchd |  |  | Name: SCHED11; Value: 10
bitfield32 | ActSchd |  |  | Name: SCHED12; Value: 11
bitfield32 | ActSchd |  |  | Name: SCHED13; Value: 12
bitfield32 | ActSchd |  |  | Name: SCHED14; Value: 13
bitfield32 | ActSchd |  |  | Name: SCHED15; Value: 14
bitfield32 | ActSchd |  |  | Name: SCHED16; Value: 15
bitfield32 | ActSchd |  |  | Name: SCHED17; Value: 16
bitfield32 | ActSchd |  |  | Name: SCHED18; Value: 17
bitfield32 | ActSchd |  |  | Name: SCHED19; Value: 18
bitfield32 | ActSchd |  |  | Name: SCHED20; Value: 19
bitfield32 | ActSchd |  |  | Name: SCHED21; Value: 20
bitfield32 | ActSchd |  |  | Name: SCHED22; Value: 21
bitfield32 | ActSchd |  |  | Name: SCHED23; Value: 22
bitfield32 | ActSchd |  |  | Name: SCHED24; Value: 23
bitfield32 | ActSchd |  |  | Name: SCHED25; Value: 24
bitfield32 | ActSchd |  |  | Name: SCHED26; Value: 25
bitfield32 | ActSchd |  |  | Name: SCHED27; Value: 26
bitfield32 | ActSchd |  |  | Name: SCHED28; Value: 27
bitfield32 | ActSchd |  |  | Name: SCHED29; Value: 28
bitfield32 | ActSchd |  |  | Name: SCHED30; Value: 29
bitfield32 | ActSchd |  |  | Name: SCHED31; Value: 30
bitfield32 | ActSchd |  |  | Name: SCHED32; Value: 31
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | IntvTyp |  |  | Name: ONETIME; Value: 0
enum16 | IntvTyp |  |  | Name: DAILY; Value: 1
enum16 | IntvTyp |  |  | Name: WEEKLY; Value: 2
enum16 | IntvTyp |  |  | Name: MONTHLY; Value: 3
enum16 | IntvTyp |  |  | Name: WEEKDAY; Value: 4
enum16 | IntvTyp |  |  | Name: HOLIDAY; Value: 5
enum16 | IntvTyp |  |  | Name: WEEKEND; Value: 6
enum16 | IntvTyp |  |  | Name: YEARLY; Value: 7
enum16 | XTyp |  |  | Name: UNSET; Value: 0
enum16 | XTyp |  |  | Name: TIME; Value: 1
enum16 | XTyp |  |  | Name: TEMP; Value: 2
enum16 | XTyp |  |  | Name: PRICE; Value: 3
enum16 | XTyp |  |  | Name: OTHER; Value: 99
enum16 | YTyp |  |  | Name: UNSET; Value: 0
enum16 | YTyp |  |  | Name: WMax; Value: 1
enum16 | YTyp |  |  | Name: RSRVD2; Value: 2
enum16 | YTyp |  |  | Name: PF; Value: 3
enum16 | YTyp |  |  | Name: RSRVD4; Value: 4
enum16 | YTyp |  |  | Name: WATT_PRICE; Value: 5
enum16 | YTyp |  |  | Name: VAR_PRICE; Value: 6
enum16 | YTyp |  |  | Name: RSRVD7; Value: 7
enum16 | YTyp |  |  | Name: VOLT_VAR_ARRAY; Value: 8
enum16 | YTyp |  |  | Name: WChaGra; Value: 9
enum16 | YTyp |  |  | Name: WDisChaGra; Value: 10
enum16 | YTyp |  |  | Name: VArAval; Value: 11
enum16 | YTyp |  |  | Name: Schedule; Value: 12
enum16 | YTyp |  |  | Name: OTHER; Value: 99

## 64200
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | REbus Device Directory | 64200 | uint16 |  |  | R | M | Device List | Use this model to to read and change the system operating mode (sysmode), determine which devices are on the REbus system, read device status updates, enable/disable devices, and get each device's Modbus Unit ID.
Header |  | 1 |  | 1 | L |  | 8 + (RB Count * 32) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | UpdtN | Update number |  | uint16 |  |  | R | M | Update Number. Incrementing number each time the mappping is changed. If the number is not changed from the last reading then none of the Modbus device addresses have changed.
Fixed Block |  | 3 | 1 | 1 | Ct | Device count |  | uint16 |  |  | R | M | The number of connected devices (and repetitions of repeating block)
Fixed Block |  | 4 | 2 | 1 | SysMd | System Operating Mode |  | enum16 |  |  | RW | M | REbus System mode (sysmode), also known as the operational mode | See X7601 Operation Manual for details on the REbus operational modes
Fixed Block |  | 5 | 3 | 1 | VT_sf | VT_sf |  | sunssf |  |  | R | M | Scale factor for V and T of repeating block
Fixed Block |  | 6 | 4 | 1 | I_sf | I_sf |  | sunssf |  |  | R | M | Scale factor for I of repeating block
Fixed Block |  | 7 | 5 | 2 | Time | Current system time |  | uint32 | s |  | R | M | Unix epoch time
Fixed Block |  | 9 | 7 | 1 | Clr | Clear device list |  | enum16 |  |  | RW | M |  | online devices will reappear momentarily after clearing
Repeating Block |  | 10 | 0 | 1 | Man | Manufacturer |  | enum16 |  |  | R | M | RCP number (manufacturer)
Repeating Block |  | 11 | 1 | 1 | Dev | Device Type |  | enum16 |  |  | R | M | RCP number (device type)
Repeating Block |  | 12 | 2 | 1 | ID | Device ID |  | uint16 |  |  | R | M | RCP number (device ID)
Repeating Block |  | 13 | 3 | 1 | Ena | Enable |  | enum16 |  |  | RW | M | enable/disable device
Repeating Block |  | 14 | 4 | 1 | UnitID | ModBus ID |  | uint16 |  |  | R | M | Modbus unit identifier
Repeating Block |  | 15 | 5 | 2 | UpdtTm | Update Time |  | uint32 | s |  | R | M | Time of last update (Unix epoch time)
Repeating Block |  | 17 | 7 | 1 | St | State |  | enum16 |  |  | R | M |  | State is a status field used by Pika Energy for operations and maintenance purposes
Repeating Block |  | 18 | 8 | 1 | P | REbus Power |  | int16 | W |  | R | M | REbus power (positive means the device is sourcing power onto REbus, negative means the device is sinking power from REbus)
Repeating Block |  | 19 | 9 | 2 | E | Accumulated Energy |  | uint32 | Wh |  | R | M | Total accumulated energy (exact definition differs by device)
Repeating Block |  | 21 | 11 | 1 | Rb | REbus Bits |  | uint16 |  |  | R | M |  | REbusBits is a status field used by Pika Energy for operations and maintenance purposes
Repeating Block |  | 22 | 12 | 1 | V | REbus Voltage |  | int16 | V | VT_sf | R | M | REbus voltage in V*10
Repeating Block |  | 23 | 13 | 1 | I | REbus Current |  | int16 | A | I_sf | R | M | REbus current in A*10
Repeating Block |  | 24 | 14 | 1 | T | Device Temperature |  | int16 | C | VT_sf | R | M | Device temperature in C*10
Repeating Block |  | 25 | 15 | 1 | O0 | Otherdata 0 |  | uint16 |  |  | R | M | Otherdata 0
Repeating Block |  | 26 | 16 | 1 | O1 | Otherdata 1 |  | uint16 |  |  | R | M | Otherdata 1
Repeating Block |  | 27 | 17 | 1 | O2 | Otherdata 2 |  | uint16 |  |  | R | M | Otherdata 2
Repeating Block |  | 28 | 18 | 1 | O3 | Otherdata 3 |  | uint16 |  |  | R | M | Otherdata 3
Repeating Block |  | 29 | 19 | 1 | O4 | Otherdata 4 |  | uint16 |  |  | R | M | Otherdata 4
Repeating Block |  | 30 | 20 | 1 | O5 | Otherdata 5 |  | uint16 |  |  | R | M | Otherdata 5
Repeating Block |  | 31 | 21 | 1 | O6 | Otherdata 6 |  | uint16 |  |  | R | M | Otherdata 6
Repeating Block |  | 32 | 22 | 1 | O7 | Otherdata 7 |  | uint16 |  |  | R | M | Otherdata 7
Repeating Block |  | 33 | 23 | 1 | O8 | Otherdata 8 |  | uint16 |  |  | R | M | Otherdata 8
Repeating Block |  | 34 | 24 | 1 | O9 | Otherdata 9 |  | uint16 |  |  | R | M | Otherdata 9
Repeating Block |  | 35 | 25 | 1 | OA | Otherdata A |  | uint16 |  |  | R | M | Otherdata A
Repeating Block |  | 36 | 26 | 1 | OB | Otherdata B |  | uint16 |  |  | R | M | Otherdata B
Repeating Block |  | 37 | 27 | 1 | OC | Otherdata C |  | uint16 |  |  | R | M | Otherdata C
Repeating Block |  | 38 | 28 | 1 | OD | Otherdata D |  | uint16 |  |  | R | M | Otherdata D
Repeating Block |  | 39 | 29 | 1 | OE | Otherdata E |  | uint16 |  |  | R | M | Otherdata E
Repeating Block |  | 40 | 30 | 1 | OF | Otherdata F |  | uint16 |  |  | R | M | Otherdata F
Repeating Block |  | 41 | 31 | 1 | OG | Otherdata G |  | uint16 |  |  | R | M | Otherdata G
enum16 | SysMd |  |  | Name: SAFETY_SHUTDOWN; Value: 0
enum16 | SysMd |  |  | Name: GRID_CONNECT; Value: 1
enum16 | SysMd |  |  | Name: SELF_SUPPLY; Value: 2
enum16 | SysMd |  |  | Name: CLEAN_BACKUP; Value: 3
enum16 | SysMd |  |  | Name: PRIORITY_BACKUP; Value: 4
enum16 | SysMd |  |  | Name: ARBITRAGE; Value: 5
enum16 | SysMd |  |  | Name: FULL_EXPORT; Value: 6
enum16 | Clr |  |  | Name: NO; Value: 0
enum16 | Clr |  |  | Name: CLEAR; Value: 1
enum16 | Man |  |  | Name: PIKA_ENERGY; Value: 1
enum16 | Dev |  |  | Name: PV_LINK; Value: 3
enum16 | Dev |  |  | Name: INVERTER; Value: 7
enum16 | Dev |  |  | Name: BATTERY; Value: 8
enum16 | Ena |  |  | Name: DISABLED; Label: disabled; Value: 16
enum16 | Ena |  |  | Name: ENABLED; Value: 1
enum16 | St |  |  | Name: UNKNOWN; Label: device offline; Value: 0
enum16 | St |  |  | Name: DISABLED; Label: disabled; Value: 16
enum16 | St |  |  | Name: INITIALIZING; Label: initializing; Value: 256
enum16 | St |  |  | Name: POWERING_UP; Label: powering up; Value: 272
enum16 | St |  |  | Name: CONNECTING_BUS; Label: connecting to REbus; Value: 288
enum16 | St |  |  | Name: DISCONNECTING_BUS; Label: disconnecting REbus; Value: 304
enum16 | St |  |  | Name: TESTING_BUS; Label: testing REbus...; Value: 320
enum16 | St |  |  | Name: LOW_BUS_VOLTAGE; Label: low REbus voltage; Value: 512
enum16 | St |  |  | Name: STANDBY; Label: standby; Value: 768
enum16 | St |  |  | Name: WAITING; Label: waiting; Value: 784
enum16 | St |  |  | Name: WAITING_NO_INPUT; Label: waiting - no input; Value: 800
enum16 | St |  |  | Name: CONNECTING_GRID; Label: connecting grid; Value: 2048
enum16 | St |  |  | Name: DISCONNECTING_GRID; Label: disconnecting grid; Value: 2064
enum16 | St |  |  | Name: GRID_CONNECTED; Label: grid connected; Value: 2080
enum16 | St |  |  | Name: ISLANDED; Label: islanded; Value: 2096
enum16 | St |  |  | Name: CONNECTING_GENERATOR; Label: connecting generator; Value: 2112
enum16 | St |  |  | Name: GENERATOR_PARALLEL; Label: generator parallel; Value: 2128
enum16 | St |  |  | Name: LOW_INPUT_VOLTAGE; Label: low input voltage; Value: 4096
enum16 | St |  |  | Name: TESTING_DEVICE_INPUT; Label: testing input...; Value: 4112
enum16 | St |  |  | Name: CONNECTING_INPUT; Label: connecting input; Value: 4352
enum16 | St |  |  | Name: DISCONNECTING_INPUT; Label: disconnecting input; Value: 4368
enum16 | St |  |  | Name: CALIBRATING; Label: calibrating; Value: 4608
enum16 | St |  |  | Name: CALIBRATION_SUCCESS; Label: calibration success!; Value: 4624
enum16 | St |  |  | Name: CALIBRATION_NEEDED; Label: calibration required; Value: 4640
enum16 | St |  |  | Name: BURN_IN; Label: burning in; Value: 4656
enum16 | St |  |  | Name: BURN_IN_DONE; Label: burn in done; Value: 4672
enum16 | St |  |  | Name: SCHEDULER_OVERRIDDEN; Label: running, overridden; Value: 4864
enum16 | St |  |  | Name: SCHEDULER_DISABLED; Label: scheduler disabled; Value: 4880
enum16 | St |  |  | Name: RUNNING; Label: running; Value: 8192
enum16 | St |  |  | Name: MAKING_POWER; Label: making power; Value: 8208
enum16 | St |  |  | Name: LIMITING_POWER; Label: limiting power; Value: 8224
enum16 | St |  |  | Name: LOW_WIND; Label: low wind; Value: 12288
enum16 | St |  |  | Name: HIGH_WIND; Label: high wind; Value: 12304
enum16 | St |  |  | Name: LOW_SUN; Label: low sun; Value: 12544
enum16 | St |  |  | Name: CHARGING_BATTERY; Label: charging; Value: 24576
enum16 | St |  |  | Name: FLOAT_CHARGING_BATTERY; Label: float charging; Value: 24592
enum16 | St |  |  | Name: BULK_CHARGING_BATTERY; Label: bulk charging; Value: 24608
enum16 | St |  |  | Name: ABSORPTION_CHARGING_BATTERY; Label: absorption charging; Value: 24624
enum16 | St |  |  | Name: EQUALIZE_CHARGING_BATTERY; Label: equalizing; Value: 24640
enum16 | St |  |  | Name: DISCHARGING_BATTERY; Label: discharging; Value: 24832
enum16 | St |  |  | Name: LOW_BATTERY_VOLTAGE; Label: low battery voltage; Value: 24848
enum16 | St |  |  | Name: ERROR_GENERIC; Label: error; Value: 28672
enum16 | St |  |  | Name: OVER_VOLTAGE_INPUT; Label: over voltage input; Value: 28688
enum16 | St |  |  | Name: OVER_VOLTAGE_OUTPUT; Label: over voltage output; Value: 28704
enum16 | St |  |  | Name: OVER_CURRENT_INPUT; Label: over current input; Value: 28720
enum16 | St |  |  | Name: OVER_CURRENT_OUTPUT; Label: over current output; Value: 28736
enum16 | St |  |  | Name: ERROR_LOW_BATTERY_VOLTAGE; Label: error: low batt volts; Value: 28752
enum16 | St |  |  | Name: OVER_TEMPERATURE; Label: over temperature; Value: 28928
enum16 | St |  |  | Name: GROUND_FAULT; Label: err: ground fault; Value: 29184
enum16 | St |  |  | Name: INSULATION_FAULT; Label: err: insulation fault; Value: 29200
enum16 | St |  |  | Name: CALIBRATION_0; Label: calibration mode; Value: 32256
enum16 | St |  |  | Name: CALIBRATION_1; Label: calibration 1; Value: 32272
enum16 | St |  |  | Name: CALIBRATION_2; Label: calibration 2; Value: 32288
enum16 | St |  |  | Name: CALIBRATION_3; Label: calibration 3; Value: 32304