## Info
Date | 2018-06-27 10:35:11
Manufacturer Name | Pika Energy
Product Name | Islanding Inverter
Product Models | X7600 Series, X11400 Series
Product Description

## 1
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40002 | ID |  |  | 1
40003 | L |  |  | 66
40004 | Manufacturer (Mn) |  |  | Pika | R
40020 | Model (Md) |  |  | X11402 Islanding Inverter | R
40036 | Options (Opt) |  |  | unimplemented | R
40044 | Version (Vr) |  |  | 132_12380 | R
40052 | Serial Number (SN) |  |  | 000100070096 | R
40068 | Device Address (DA) |  |  | 70 | RW
40069 | Pad |  |  |  | R

## 64207
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40070 | ID |  |  | 64207
40071 | L |  |  | 12
40072 | REbus Power (P) |  |  | supported | R
40073 | Accumulated Energy (E) |  |  | supported | R
40075 | REbus Voltage (V) |  |  | supported | R
40076 | REbus Current (I) |  |  | supported | R
40077 | Device Temperature (T) |  |  | supported | R
40078 | State (St) |  |  | supported | R
|  |  | device offline (UNKNOWN) | supported
|  |  | disabled (DISABLED) | supported
|  |  | initializing (INITIALIZING) | supported
|  |  | powering up (POWERING_UP) | supported
|  |  | connecting to REbus (CONNECTING_BUS) | supported
|  |  | disconnecting REbus (DISCONNECTING_BUS) | supported
|  |  | testing REbus... (TESTING_BUS) | supported
|  |  | low REbus voltage (LOW_BUS_VOLTAGE) | supported
|  |  | standby (STANDBY) | supported
|  |  | waiting (WAITING) | supported
|  |  | waiting - no input (WAITING_NO_INPUT) | supported
|  |  | connecting grid (CONNECTING_GRID) | supported
|  |  | disconnecting grid (DISCONNECTING_GRID) | supported
|  |  | grid connected (GRID_CONNECTED) | supported
|  |  | islanded (ISLANDED) | supported
|  |  | connecting generator (CONNECTING_GENERATOR) | supported
|  |  | generator parallel (GENERATOR_PARALLEL) | supported
|  |  | low input voltage (LOW_INPUT_VOLTAGE) | supported
|  |  | testing input... (TESTING_DEVICE_INPUT) | supported
|  |  | connecting input (CONNECTING_INPUT) | supported
|  |  | disconnecting input (DISCONNECTING_INPUT) | supported
|  |  | calibrating (CALIBRATING) | supported
|  |  | calibration success! (CALIBRATION_SUCCESS) | supported
|  |  | calibration required (CALIBRATION_NEEDED) | supported
|  |  | burning in (BURN_IN) | supported
|  |  | burn in done (BURN_IN_DONE) | supported
|  |  | running, overridden (SCHEDULER_OVERRIDDEN) | supported
|  |  | scheduler disabled (SCHEDULER_DISABLED) | supported
|  |  | running (RUNNING) | supported
|  |  | making power (MAKING_POWER) | supported
|  |  | limiting power (LIMITING_POWER) | supported
|  |  | low wind (LOW_WIND) | supported
|  |  | high wind (HIGH_WIND) | supported
|  |  | low sun (LOW_SUN) | supported
|  |  | charging (CHARGING_BATTERY) | supported
|  |  | float charging (FLOAT_CHARGING_BATTERY) | supported
|  |  | bulk charging (BULK_CHARGING_BATTERY) | supported
|  |  | absorption charging (ABSORPTION_CHARGING_BATTERY) | supported
|  |  | equalizing (EQUALIZE_CHARGING_BATTERY) | supported
|  |  | discharging (DISCHARGING_BATTERY) | supported
|  |  | low battery voltage (LOW_BATTERY_VOLTAGE) | supported
|  |  | error (ERROR_GENERIC) | supported
|  |  | over voltage input (OVER_VOLTAGE_INPUT) | supported
|  |  | over voltage output (OVER_VOLTAGE_OUTPUT) | supported
|  |  | over current input (OVER_CURRENT_INPUT) | supported
|  |  | over current output (OVER_CURRENT_OUTPUT) | supported
|  |  | error: low batt volts (ERROR_LOW_BATTERY_VOLTAGE) | supported
|  |  | over temp shutdown (OVER_TEMPERATURE) | supported
|  |  | ground fault (GROUND_FAULT) | supported
|  |  | err: insulation fault (INSULATION_FAULT) | supported
|  |  | calibration mode (CALIBRATION_0) | supported
|  |  | calibration 1 (CALIBRATION_1) | supported
|  |  | calibration 2 (CALIBRATION_2) | supported
|  |  | calibration 3 (CALIBRATION_3) | supported
40079 | Last Event (Ev) |  |  | supported | R
|  |  | unknown event (GENERIC) | supported
|  |  | power up (POWERUP) | supported
|  |  | supply under voltage (SUPPLY_UNDERVOLTAGE) | supported
|  |  | daily event (DAILY_EVENT) | supported
|  |  | enable (ENABLE) | supported
|  |  | disable (DISABLE) | supported
|  |  | manual disable (MANUAL_DISABLE) | supported
|  |  | external estop (EXTERNAL_ESTOP) | supported
|  |  | sysmode change (SYSMODE_CHANGE) | supported
|  |  | unauthorized sysmode (SYSMODE_BAD) | supported
|  |  | debug trace recorded (DEBUG_TRACE) | supported
|  |  | TOU entry activated (TOU_ENTRY_ACTIVATED) | supported
|  |  | software version (SOFTWARE_VERSION) | supported
|  |  | hardware version mismatch (HARDWARE_VERSION) | supported
|  |  | interrupt fault (INTERRUPT_FAULT) | supported
|  |  | gate drive fault (GATEDRIVE_FAULT) | supported
|  |  | timer fault (TIMER_FAULT) | supported
|  |  | transistor failure (TRANSISTOR_FAILURE) | supported
|  |  | over temp shutdown (OVER_TEMPERATURE) | supported
|  |  | fan failure (FAN_FAILURE) | supported
|  |  | fuse blown (FUSE_BLOWN) | supported
|  |  | miswiring fault (MISWIRING) | supported
|  |  | alternator bad (ALTERNATOR_BAD) | supported
|  |  | reverse rotation (REVERSE_ROTATION) | supported
|  |  | REbus fault (BUS_FAULT) | supported
|  |  | REbus no load (BUS_NO_LOAD) | supported
|  |  | REbus over voltage (BUS_OVER_VOLTAGE) | supported
|  |  | REbus under voltage (BUS_UNDER_VOLTAGE) | supported
|  |  | REbus over current (BUS_OVER_CURRENT) | supported
|  |  | internal over voltage (INTERNAL_OVERVOLTAGE) | supported
|  |  | battery generic (BATTERY_GENERIC) | supported
|  |  | battery ready (BATTERY_READY) | supported
|  |  | battery not ready (BATTERY_NOT_READY) | supported
|  |  | BMS generic (BMS_GENERIC) | supported
|  |  | BMS alarm (BMS_ALARM) | supported
|  |  | BMS warning (BMS_WARNING) | supported
|  |  | BMS error (BMS_ERROR) | supported
|  |  | ground fault (GROUND_FAULT) | supported
|  |  | input low (INPUT_LOW) | supported
|  |  | input sensor fault (INPUT_SENSOR_FAULT) | supported
|  |  | input over current (INPUT_OVER_CURRENT) | supported
|  |  | input overspeed (INPUT_OVERSPEED) | supported
|  |  | input high (INPUT_HIGH) | supported
|  |  | arc fault (ARC_FAULT) | supported
|  |  | input ready (INPUT_READY) | supported
|  |  | grid fault (GRID_FAULT) | supported
|  |  | grid over voltage (GRID_OVER_VOLTAGE) | supported
|  |  | grid over current (GRID_OVER_CURRENT) | supported
|  |  | grid over frequency (GRID_OVER_FREQUENCY) | supported
|  |  | grid under voltage (GRID_UNDER_VOLTAGE) | supported
|  |  | grid under frequency (GRID_UNDER_FREQUENCY) | supported
|  |  | grid overvoltage fast (GRID_OVER_VOLTAGE_FAST) | supported
|  |  | grid high impedance (GRID_HIGH_IMPEDANCE) | supported
|  |  | transfer sw fail (TRANSFER_FAIL) | supported
|  |  | setpoint crc fault (SETPOINT_CRC_FAULT) | supported
|  |  | EEPROM failure (EEPROM_FAULT) | supported
|  |  | FLASH fault (FLASH_FAULT) | supported
|  |  | PLM restart (PLM_RESTART) | supported
|  |  | default trap (DEFAULT_TRAP) | supported
|  |  | address error trap (ADDRESS_ERROR) | supported
|  |  | stack error trap (STACK_ERROR) | supported
|  |  | osc. fail trap (OSCILLATOR_FAIL) | supported
|  |  | math error trap (MATH_ERROR) | supported
|  |  | dmac error trap (DMAC_ERROR) | supported
40080 | REbusBits (RB) |  |  | supported | R
|  |  | ENABLE_MASTER | supported
|  |  | ENABLE_SOURCE | supported
|  |  | ENABLE_SINK | supported
|  |  | REBUS_CONNECTED | supported
|  |  | SOURCING | supported
|  |  | SINKING | supported
|  |  | limiting power (LIMITING_POWER) | supported
|  |  | TEMP_LIMIT | supported
|  |  | BUS_VOLTAGE_LOW | supported
|  |  | DEV_VOLTAGE_LOW | supported
|  |  | BUS_VOLTAGE_HIGH | supported
|  |  | DEV_VOLTAGE_HIGH | supported
|  |  | TEMPERATURE_HIGH | supported
|  |  | SPT_INVALID | supported
|  |  | GROUNDFAULT | supported
|  |  | SUPPLY_VOLTAGE_LOW | supported
40081 | VT_sf |  |  | -1 | R
40082 | I_sf |  |  | -2 | R
40083 | Pad0 |  |  |  | R

## 64208
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40084 | ID |  |  | 64208
40085 | L |  |  | 22
40086 | System Operating Mode (SysMd) |  |  | supported | R
|  |  | Saftey Shutdown (SAFETY_SHUTDOWN) | supported
|  |  | Grid Tie (GRID_TIE) | supported
|  |  | Self Supply (SELF_SUPPLY) | supported
|  |  | Clean Backup (CLEAN_BACKUP) | supported
|  |  | Priority Backup (PRIORITY_BACKUP) | supported
|  |  | REMOTE_ARBITRAGE | supported
|  |  | Sell (SELL) | supported
40087 | External CT Power measurement (CTPow) |  |  | supported | R
40088 | Total AC Energy Imported (WhIn) |  |  | supported | R
40090 | Total AC Energy Exported (WhOut) |  |  | supported | R
40092 | Error status (ErrorWord) |  |  | supported | R
|  |  | LINE1_OVERCURRENT | supported
|  |  | AC_PRECHARGE_FAIL | supported
|  |  | DC_OVERCURRENT | supported
|  |  | DC_UNBALANCED_CURRENT | supported
|  |  | GATEDRIVE_FAULT | supported
|  |  | BAD_THERMISTER | supported
|  |  | OVERTEMP_COMP | supported
|  |  | DC_PRECHARGE_FAIL | supported
|  |  | XFR_SWITCH_FAIL | supported
|  |  | FLASH_FAIL | supported
|  |  | EEPROM_FAIL | supported
|  |  | AINV_INVALID | supported
40093 | Enable bits (EnableBits) |  |  | supported | R
|  |  | DEADMAN | supported
|  |  | DEADMAN_UP | supported
|  |  | UNLOCK_GRIDSYNC | supported
|  |  | CTCAL | supported
|  |  | REBUS_CONNECT | supported
|  |  | GRID_DISCONNECT | supported
|  |  | OUTPUT_CONNECT | supported
|  |  | LINE3_CONNECT | supported
|  |  | VOLTAGE_MODE | supported
|  |  | CURRENT_MODE | supported
|  |  | BRIDGE | supported
|  |  | NEUT_BRIDGE | supported
|  |  | UNUSED12 | supported
|  |  | AUTOFAN_ON | supported
|  |  | LCM_RCP | supported
|  |  | USB_RCP | supported
40094 | Relay status (RelayStatus) |  |  | supported | R
|  |  | AC_PRECHARGE | supported
|  |  | DC_PRECHARGE | supported
|  |  | REBUS_CONNECTED | supported
|  |  | REBUS_DISCONNETED | supported
|  |  | GRID_CONNECTED | supported
|  |  | GRID_DISCONNECTED | supported
|  |  | OUTPUT_CONNECTED | supported
|  |  | OUTPUT_DISCONNECTED | supported
|  |  | LINE3_CONNECTED | supported
|  |  | LINE3_DISCONNECTED | supported
|  |  | LINE3_RETURNING | supported
|  |  | UNUSED11 | supported
|  |  | UNUSED12 | supported
|  |  | UNUSED13 | supported
|  |  | UNUSED14 | supported
|  |  | UNUSED15 | supported
40095 | General status (StatusWord) |  |  | supported | R
|  |  | V1_LOCKED | supported
|  |  | V2_LOCKED | supported
|  |  | FREQ_LOCKED | supported
|  |  | PHASE_LOCKED | supported
|  |  | LOCKED_TO_GRID | supported
|  |  | PRERES_OVERTEMP | supported
|  |  | QPRIORITY | supported
|  |  | EXT_TRANSFERRED | supported
|  |  | MFLT_ACTIVE | supported
|  |  | ESTOP_ACTIVE | supported
|  |  | GF_ACTIVE | supported
|  |  | AF_ACTIVE | supported
|  |  | PLM_READY | supported
|  |  | INST_IFACE | supported
|  |  | XESTOP_ACTIVE | supported
|  |  | UNUSED15 | supported
40096 | AC Line Status (LineStatus) |  |  | supported | R
|  |  | V1_LOW | supported
|  |  | V1_HIGH | supported
|  |  | V2_LOW | supported
|  |  | V2_HIGH | supported
|  |  | V3_LOW | supported
|  |  | V3_HIGH | supported
|  |  | FREQ_LOW | supported
|  |  | FREQ_HIGH | supported
|  |  | UNLOCK | supported
|  |  | NO_ZCROSS | supported
|  |  | HIGH_IMP | supported
|  |  | GRIDFAULT | supported
|  |  | GT_SPLIT_OR_REVERSE | supported
|  |  | GT_3PHASE | supported
|  |  | CESSATION | supported
|  |  | GENMODE | supported
40097 | Pad (Pad0) |  |  |  | R
40098 | Pad1 |  |  |  | R
40099 | Pad2 |  |  |  | R
40100 | Pad3 |  |  |  | R
40101 | Pad4 |  |  |  | R
40102 | Pad5 |  |  |  | R
40103 | Pad6 |  |  |  | R
40104 | Pad7 |  |  |  | R
40105 | Pad8 |  |  |  | R
40106 | Pad9 |  |  |  | R
40107 | Pad10 |  |  |  | R

## 64206
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40108 | ID |  |  | 64206
40109 | L |  |  | 46
40110 | Enable inverter (Conn) |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40111 | Access code (Pwd) |  |  | supported | RW
40115 | Compliance selection (SRD) |  |  |  | R
|  |  | IEEE_1547 | supported
|  |  | RULE_14H_1 | supported
|  |  | RULE_14H_2 | supported
|  |  | RULE_21 | supported
|  |  | RULE_PREPA | supported
40116 | Compliance settings defaulted (Def) |  |  |  | R
|  |  | NOT_DEFAULTED | supported
|  |  | DEFAULTED | supported
40117 | Zero Export (ZExp) |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40118 | Enable Islanding (IslandEna) |  |  | supported | RW
|  |  | ISLANDING_DISABLED | supported
|  |  | ISLANDING_ENABLED | supported
40119 | Enabled SysModes (ActSysMds) |  |  | supported | RW
|  |  | SAFETY_SHUTDOWN | supported
|  |  | GRID_TIE | supported
|  |  | SELF_SUPPLY | supported
|  |  | CLEAN_BACKUP | supported
|  |  | PRIORITY_BACKUP | supported
|  |  | REMOTE_ARBITRAGE | supported
|  |  | SELL | supported
40120 | Trigger CT calibration (CTTrig) |  |  | supported | RW
|  |  | AUTO | supported
|  |  | TRIGGER | supported
40121 | Clear display (ClrDisp) |  |  | supported | RW
|  |  | NO | supported
|  |  | CLEAR | supported
40122 | PLM channel (PLMCh) |  |  | supported | RW
|  |  | CH_0 | supported
|  |  | CH_1 | supported
|  |  | CH_2 | supported
|  |  | CH_3 | supported
|  |  | CH_4 | supported
|  |  | CH_5 | supported
|  |  | CH_6 | supported
|  |  | CH_7 | supported
|  |  | CH_8 | supported
|  |  | CH_9 | supported
|  |  | CH_10 | supported
|  |  | CH_11 | supported
|  |  | CH_12 | supported
40123 | PLM enable (PLMEna) |  |  | supported | RW
|  |  | PLM_DISABLED | supported
|  |  | PLM_ENABLED | supported
40124 | Global PLM Reset (GPLMRst) |  |  | unimplemented | RW
|  |  | RESET | supported
40125 | PLM Group Set (GPLMCh) |  |  | unimplemented | RW
|  |  | NONE | supported
|  |  | CH_1 | supported
|  |  | CH_2 | supported
|  |  | CH_3 | supported
|  |  | CH_4 | supported
|  |  | CH_5 | supported
|  |  | CH_6 | supported
|  |  | CH_7 | supported
|  |  | CH_8 | supported
|  |  | CH_9 | supported
|  |  | CH_10 | supported
|  |  | CH_11 | supported
|  |  | CH_12 | supported
40126 | Self Supply Source Power (SS_Src) |  |  | supported | RW
40127 | Self Supply Sink Power (SS_Sink) |  |  | supported | RW
40128 | Enable External Transfer (XFREna) |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40129 | XFRV_sf |  |  | -1 | R
40130 | External Transfer Voltage (XFRV) |  |  | supported | RW
40131 | External Transfer timeout (XFRTms) |  |  | supported | RW
40132 | Pad (Pad0) |  |  |  | R
40133 | Pad1 |  |  |  | R
40134 | Pad2 |  |  |  | R
40135 | Pad3 |  |  |  | R
40136 | Pad4 |  |  |  | R
40137 | Pad5 |  |  |  | R
40138 | Pad6 |  |  |  | R
40139 | Pad7 |  |  |  | R
40140 | Pad8 |  |  |  | R
40141 | Pad9 |  |  |  | R
40142 | Pad10 |  |  |  | R
40143 | Pad11 |  |  |  | R
40144 | Pad12 |  |  |  | R
40145 | Pad13 |  |  |  | R
40146 | Pad14 |  |  |  | R
40147 | Pad15 |  |  |  | R
40148 | Pad16 |  |  |  | R
40149 | Pad17 |  |  |  | R
40150 | Pad18 |  |  |  | R
40151 | Pad19 |  |  |  | R
40152 | Pad20 |  |  |  | R
40153 | Pad21 |  |  |  | R
40154 | Pad22 |  |  |  | R
40155 | Pad23 |  |  |  | R

## 102
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40156 | ID |  |  | 102
40157 | L |  |  | 50
40158 | Amps (A) |  |  | supported | R
40159 | Amps PhaseA (AphA) |  |  | supported | R
40160 | Amps PhaseB (AphB) |  |  | supported | R
40161 | Amps PhaseC (AphC) |  |  | unimplemented | R
40162 | A_SF |  |  | -2 | R
40163 | Phase Voltage AB (PPVphAB) |  |  | unimplemented | R
40164 | Phase Voltage BC (PPVphBC) |  |  | unimplemented | R
40165 | Phase Voltage CA (PPVphCA) |  |  | unimplemented | R
40166 | Phase Voltage AN (PhVphA) |  |  | supported | R
40167 | Phase Voltage BN (PhVphB) |  |  | supported | R
40168 | Phase Voltage CN (PhVphC) |  |  | unimplemented | R
40169 | V_SF |  |  | -1 | R
40170 | Watts (W) |  |  | supported | R
40171 | W_SF |  |  | 0 | R
40172 | Hz |  |  | supported | R
40173 | Hz_SF |  |  | -2 | R
40174 | VA |  |  | supported | R
40175 | VA_SF |  |  | 0 | R
40176 | VAr |  |  | supported | R
40177 | VAr_SF |  |  | 0 | R
40178 | PF |  |  | supported | R
40179 | PF_SF |  |  | -1 | R
40180 | WattHours (WH) |  |  | supported | R
40182 | WH_SF |  |  | 0 | R
40183 | DC Amps (DCA) |  |  | unimplemented | R
40184 | DCA_SF |  |  | 0 | R
40185 | DC Voltage (DCV) |  |  | supported | R
40186 | DCV_SF |  |  | -1 | R
40187 | DC Watts (DCW) |  |  | unimplemented | R
40188 | DCW_SF |  |  | 0 | R
40189 | Cabinet Temperature (TmpCab) |  |  | supported | R
40190 | Heat Sink Temperature (TmpSnk) |  |  | supported | R
40191 | Transformer Temperature (TmpTrns) |  |  | supported | R
40192 | Other Temperature (TmpOt) |  |  | supported | R
40193 | Tmp_SF |  |  | -1 | R
40194 | Operating State (St) |  |  | supported | R
|  |  | Off (OFF) | supported
|  |  | Sleeping (SLEEPING) | supported
|  |  | Starting (STARTING) | supported
|  |  | MPPT | supported
|  |  | Throttled (THROTTLED) | supported
|  |  | Shutting down (SHUTTING_DOWN) | supported
|  |  | Fault (FAULT) | supported
|  |  | Standby (STANDBY) | supported
40195 | Vendor Operating State (StVnd) |  |  | supported | R
40196 | Event1 (Evt1) |  |  | supported | R
|  |  | Ground fault (GROUND_FAULT) | supported
|  |  | DC over voltage (DC_OVER_VOLT) | supported
|  |  | AC disconnect open (AC_DISCONNECT) | supported
|  |  | DC disconnect open (DC_DISCONNECT) | supported
|  |  | Grid shutdown (GRID_DISCONNECT) | supported
|  |  | Cabinet open (CABINET_OPEN) | supported
|  |  | Manual shutdown (MANUAL_SHUTDOWN) | supported
|  |  | Over temperature (OVER_TEMP) | supported
|  |  | Frequency above limit (OVER_FREQUENCY) | supported
|  |  | Frequency under limit (UNDER_FREQUENCY) | supported
|  |  | AC Voltage above limit (AC_OVER_VOLT) | supported
|  |  | AC Voltage under limit (AC_UNDER_VOLT) | supported
|  |  | Blown String fuse on input (BLOWN_STRING_FUSE) | supported
|  |  | Under temperature (UNDER_TEMP) | supported
|  |  | Generic Memory or Communication error (internal) (MEMORY_LOSS) | supported
|  |  | Hardware test failure (HW_TEST_FAILURE) | supported
40198 | Event Bitfield 2 (Evt2) |  |  | supported | R
40200 | Vendor Event Bitfield 1 (EvtVnd1) |  |  | supported | R
40202 | Vendor Event Bitfield 2 (EvtVnd2) |  |  | supported | R
40204 | Vendor Event Bitfield 3 (EvtVnd3) |  |  | supported | R
40206 | Vendor Event Bitfield 4 (EvtVnd4) |  |  | supported | R

## 64204
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40208 | ID |  |  | 64204
40209 | L |  |  | 8
40210 | Power export line 1 (Px1) |  |  | supported | R
40211 | Power export line 2 (Px2) |  |  | supported | R
40212 | Power export line 3 (Px3) |  |  | supported | R
40213 | Energy exported (Whx) |  |  | supported | R
40215 | Energy imported (Whin) |  |  | supported | R
40217 | Pad |  |  |  | R

## 64202
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40218 | ID |  |  | 64202
40219 | L |  |  | 12
40220 | System Operating Mode (SysMd) |  |  | supported | R
|  |  | SAFETY_SHUTDOWN | supported
|  |  | GRID_CONNECT | supported
|  |  | SELF_SUPPLY | supported
|  |  | CLEAN_BACKUP | supported
|  |  | PRIORITY_BACKUP | supported
|  |  | ARBITRAGE | supported
40221 | Max real power (PMax) |  |  | supported | RW
40222 | Max reactive power (QMax) |  |  | supported | RW
40223 | Real power target (PMaxLimPct) |  |  | supported | RW
40224 | Reactive power target (QMaxLimPct) |  |  | supported | RW
40225 | Ramp rate (PQGra) |  |  | supported | RW
40226 | PQMax_SF |  |  | 0 | R
40227 | PQLimPct_SF |  |  | -1 | R
40228 | PQGra_SF |  |  | -1 | R
40229 | Control priority (CtlPr) |  |  | supported | RW
|  |  | REAL | supported
|  |  | REACTIVE | supported
40230 | Enable arbitrage control (PQSet_Ena) |  |  | supported | RW
|  |  | DISABLE | supported
|  |  | ENABLE | supported
|  |  | UPDATE | supported
40231 | Connect (Conn) |  |  | supported | RW
|  |  | DISCONNECT | supported
|  |  | CONNECT | supported

## 64205
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40232 | ID |  |  | 64205
40233 | L |  |  | 2
40234 | Compliance selection (SRD) |  |  | supported | RW
|  |  | IEEE_1547 | supported
|  |  | RULE_14H_1 | supported
|  |  | RULE_14H_2 | supported
|  |  | RULE_21 | supported
|  |  | RULE_PREPA | supported
40235 | Defaulted (Def) |  |  | supported | R
|  |  | NOT_DEFAULTED | supported
|  |  | DEFAULTED | supported

## 120
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40236 | ID |  |  | 120
40237 | L |  |  | 26
40238 | DERTyp |  |  | supported | R
|  |  | PV | supported
|  |  | PV_STOR | supported
40239 | WRtg |  |  | supported | R
40240 | WRtg_SF |  |  | 0 | R
40241 | VARtg |  |  | supported | R
40242 | VARtg_SF |  |  | 0 | R
40243 | VArRtgQ1 |  |  | supported | R
40244 | VArRtgQ2 |  |  | supported | R
40245 | VArRtgQ3 |  |  | supported | R
40246 | VArRtgQ4 |  |  | supported | R
40247 | VArRtg_SF |  |  | 0 | R
40248 | ARtg |  |  | supported | R
40249 | ARtg_SF |  |  | -2 | R
40250 | PFRtgQ1 |  |  | supported | R
40251 | PFRtgQ2 |  |  | supported | R
40252 | PFRtgQ3 |  |  | supported | R
40253 | PFRtgQ4 |  |  | supported | R
40254 | PFRtg_SF |  |  | -3 | R
40255 | WHRtg |  |  | unimplemented | R
40256 | WHRtg_SF |  |  | 0 | R
40257 | AhrRtg |  |  | unimplemented | R
40258 | AhrRtg_SF |  |  | 0 | R
40259 | MaxChaRte |  |  | unimplemented | R
40260 | MaxChaRte_SF |  |  | 0 | R
40261 | MaxDisChaRte |  |  | unimplemented | R
40262 | MaxDisChaRte_SF |  |  | 0 | R
40263 | Pad |  |  |  | R

## 123
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40264 | ID |  |  | 123
40265 | L |  |  | 24
40266 | Conn_WinTms |  |  | unimplemented | RW
40267 | Conn_RvrtTms |  |  | unimplemented | RW
40268 | Conn |  |  | supported | RW
|  |  | DISCONNECT | supported
|  |  | CONNECT | supported
40269 | WMaxLimPct |  |  | supported | RW
40270 | WMaxLimPct_WinTms |  |  | unimplemented | RW
40271 | WMaxLimPct_RvrtTms |  |  | unimplemented | RW
40272 | WMaxLimPct_RmpTms |  |  | unimplemented | RW
40273 | WMaxLim_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40274 | OutPFSet |  |  | supported | RW
40275 | OutPFSet_WinTms |  |  | unimplemented | RW
40276 | OutPFSet_RvrtTms |  |  | unimplemented | RW
40277 | OutPFSet_RmpTms |  |  | unimplemented | RW
40278 | OutPFSet_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40279 | VArWMaxPct |  |  | unimplemented | RW
40280 | VArMaxPct |  |  | supported | RW
40281 | VArAvalPct |  |  | unimplemented | RW
40282 | VArPct_WinTms |  |  | unimplemented | RW
40283 | VArPct_RvrtTms |  |  | unimplemented | RW
40284 | VArPct_RmpTms |  |  | unimplemented | RW
40285 | VArPct_Mod |  |  | unimplemented | RW
|  |  | NONE | supported
|  |  | WMax | supported
|  |  | VArMax | supported
|  |  | VArAval | supported
40286 | VArPct_Ena |  |  | supported | RW
|  |  | DISABLED | supported
|  |  | ENABLED | supported
40287 | WMaxLimPct_SF |  |  | -1 | R
40288 | OutPFSet_SF |  |  | -3 | R
40289 | VArPct_SF |  |  | -1 | R

## 126
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40290 | ID |  |  | 126
40291 | L |  |  | 226
40292 | ActCrv |  |  | supported | RW
40293 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40294 | WinTms |  |  | unimplemented | RW
40295 | RvrtTms |  |  | unimplemented | RW
40296 | RmpTms |  |  | unimplemented | RW
40297 | NCrv |  |  | supported | R
40298 | NPt |  |  | supported | R
40299 | V_SF |  |  | -1 | R
40300 | DeptRef_SF |  |  | -1 | R
40301 | RmpIncDec_SF |  |  | 0 | R
40302 | ActPt | 1 |  | supported | RW
40303 | DeptRef | 1 |  | supported | RW
|  |  | WMax | supported
|  |  | VArMax | supported
|  |  | VArAval | supported
40304 | V1 | 1 |  | supported | RW
40305 | VAr1 | 1 |  | supported | RW
40306 | V2 | 1 |  | supported | RW
40307 | VAr2 | 1 |  | supported | RW
40308 | V3 | 1 |  | supported | RW
40309 | VAr3 | 1 |  | supported | RW
40310 | V4 | 1 |  | supported | RW
40311 | VAr4 | 1 |  | supported | RW
40312 | V5 | 1 |  | unimplemented | RW
40313 | VAr5 | 1 |  | unimplemented | RW
40314 | V6 | 1 |  | unimplemented | RW
40315 | VAr6 | 1 |  | unimplemented | RW
40316 | V7 | 1 |  | unimplemented | RW
40317 | VAr7 | 1 |  | unimplemented | RW
40318 | V8 | 1 |  | unimplemented | RW
40319 | VAr8 | 1 |  | unimplemented | RW
40320 | V9 | 1 |  | unimplemented | RW
40321 | VAr9 | 1 |  | unimplemented | RW
40322 | V10 | 1 |  | unimplemented | RW
40323 | VAr10 | 1 |  | unimplemented | RW
40324 | V11 | 1 |  | unimplemented | RW
40325 | VAr11 | 1 |  | unimplemented | RW
40326 | V12 | 1 |  | unimplemented | RW
40327 | VAr12 | 1 |  | unimplemented | RW
40328 | V13 | 1 |  | unimplemented | RW
40329 | VAr13 | 1 |  | unimplemented | RW
40330 | V14 | 1 |  | unimplemented | RW
40331 | VAr14 | 1 |  | unimplemented | RW
40332 | V15 | 1 |  | unimplemented | RW
40333 | VAr15 | 1 |  | unimplemented | RW
40334 | V16 | 1 |  | unimplemented | RW
40335 | VAr16 | 1 |  | unimplemented | RW
40336 | V17 | 1 |  | unimplemented | RW
40337 | VAr17 | 1 |  | unimplemented | RW
40338 | V18 | 1 |  | unimplemented | RW
40339 | VAr18 | 1 |  | unimplemented | RW
40340 | V19 | 1 |  | unimplemented | RW
40341 | VAr19 | 1 |  | unimplemented | RW
40342 | V20 | 1 |  | unimplemented | RW
40343 | VAr20 | 1 |  | unimplemented | RW
40344 | CrvNam | 1 |  | unimplemented | RW
40352 | RmpTms | 1 |  | unimplemented | RW
40353 | RmpDecTmm | 1 |  | unimplemented | RW
40354 | RmpIncTmm | 1 |  | unimplemented | RW
40355 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
40356 | ActPt | 2 |  | supported | RW
40357 | DeptRef | 2 |  | supported | RW
40358 | V1 | 2 |  | supported | RW
40359 | VAr1 | 2 |  | supported | RW
40360 | V2 | 2 |  | supported | RW
40361 | VAr2 | 2 |  | supported | RW
40362 | V3 | 2 |  | supported | RW
40363 | VAr3 | 2 |  | supported | RW
40364 | V4 | 2 |  | supported | RW
40365 | VAr4 | 2 |  | supported | RW
40366 | V5 | 2 |  | unimplemented | RW
40367 | VAr5 | 2 |  | unimplemented | RW
40368 | V6 | 2 |  | unimplemented | RW
40369 | VAr6 | 2 |  | unimplemented | RW
40370 | V7 | 2 |  | unimplemented | RW
40371 | VAr7 | 2 |  | unimplemented | RW
40372 | V8 | 2 |  | unimplemented | RW
40373 | VAr8 | 2 |  | unimplemented | RW
40374 | V9 | 2 |  | unimplemented | RW
40375 | VAr9 | 2 |  | unimplemented | RW
40376 | V10 | 2 |  | unimplemented | RW
40377 | VAr10 | 2 |  | unimplemented | RW
40378 | V11 | 2 |  | unimplemented | RW
40379 | VAr11 | 2 |  | unimplemented | RW
40380 | V12 | 2 |  | unimplemented | RW
40381 | VAr12 | 2 |  | unimplemented | RW
40382 | V13 | 2 |  | unimplemented | RW
40383 | VAr13 | 2 |  | unimplemented | RW
40384 | V14 | 2 |  | unimplemented | RW
40385 | VAr14 | 2 |  | unimplemented | RW
40386 | V15 | 2 |  | unimplemented | RW
40387 | VAr15 | 2 |  | unimplemented | RW
40388 | V16 | 2 |  | unimplemented | RW
40389 | VAr16 | 2 |  | unimplemented | RW
40390 | V17 | 2 |  | unimplemented | RW
40391 | VAr17 | 2 |  | unimplemented | RW
40392 | V18 | 2 |  | unimplemented | RW
40393 | VAr18 | 2 |  | unimplemented | RW
40394 | V19 | 2 |  | unimplemented | RW
40395 | VAr19 | 2 |  | unimplemented | RW
40396 | V20 | 2 |  | unimplemented | RW
40397 | VAr20 | 2 |  | unimplemented | RW
40398 | CrvNam | 2 |  | unimplemented | RW
40406 | RmpTms | 2 |  | unimplemented | RW
40407 | RmpDecTmm | 2 |  | unimplemented | RW
40408 | RmpIncTmm | 2 |  | unimplemented | RW
40409 | ReadOnly | 2 |  | supported | R
40410 | ActPt | 3 |  | supported | RW
40411 | DeptRef | 3 |  | supported | RW
40412 | V1 | 3 |  | supported | RW
40413 | VAr1 | 3 |  | supported | RW
40414 | V2 | 3 |  | supported | RW
40415 | VAr2 | 3 |  | supported | RW
40416 | V3 | 3 |  | supported | RW
40417 | VAr3 | 3 |  | supported | RW
40418 | V4 | 3 |  | supported | RW
40419 | VAr4 | 3 |  | supported | RW
40420 | V5 | 3 |  | unimplemented | RW
40421 | VAr5 | 3 |  | unimplemented | RW
40422 | V6 | 3 |  | unimplemented | RW
40423 | VAr6 | 3 |  | unimplemented | RW
40424 | V7 | 3 |  | unimplemented | RW
40425 | VAr7 | 3 |  | unimplemented | RW
40426 | V8 | 3 |  | unimplemented | RW
40427 | VAr8 | 3 |  | unimplemented | RW
40428 | V9 | 3 |  | unimplemented | RW
40429 | VAr9 | 3 |  | unimplemented | RW
40430 | V10 | 3 |  | unimplemented | RW
40431 | VAr10 | 3 |  | unimplemented | RW
40432 | V11 | 3 |  | unimplemented | RW
40433 | VAr11 | 3 |  | unimplemented | RW
40434 | V12 | 3 |  | unimplemented | RW
40435 | VAr12 | 3 |  | unimplemented | RW
40436 | V13 | 3 |  | unimplemented | RW
40437 | VAr13 | 3 |  | unimplemented | RW
40438 | V14 | 3 |  | unimplemented | RW
40439 | VAr14 | 3 |  | unimplemented | RW
40440 | V15 | 3 |  | unimplemented | RW
40441 | VAr15 | 3 |  | unimplemented | RW
40442 | V16 | 3 |  | unimplemented | RW
40443 | VAr16 | 3 |  | unimplemented | RW
40444 | V17 | 3 |  | unimplemented | RW
40445 | VAr17 | 3 |  | unimplemented | RW
40446 | V18 | 3 |  | unimplemented | RW
40447 | VAr18 | 3 |  | unimplemented | RW
40448 | V19 | 3 |  | unimplemented | RW
40449 | VAr19 | 3 |  | unimplemented | RW
40450 | V20 | 3 |  | unimplemented | RW
40451 | VAr20 | 3 |  | unimplemented | RW
40452 | CrvNam | 3 |  | unimplemented | RW
40460 | RmpTms | 3 |  | unimplemented | RW
40461 | RmpDecTmm | 3 |  | unimplemented | RW
40462 | RmpIncTmm | 3 |  | unimplemented | RW
40463 | ReadOnly | 3 |  | supported | R
40464 | ActPt | 4 |  | supported | RW
40465 | DeptRef | 4 |  | supported | RW
40466 | V1 | 4 |  | supported | RW
40467 | VAr1 | 4 |  | supported | RW
40468 | V2 | 4 |  | supported | RW
40469 | VAr2 | 4 |  | supported | RW
40470 | V3 | 4 |  | supported | RW
40471 | VAr3 | 4 |  | supported | RW
40472 | V4 | 4 |  | supported | RW
40473 | VAr4 | 4 |  | supported | RW
40474 | V5 | 4 |  | unimplemented | RW
40475 | VAr5 | 4 |  | unimplemented | RW
40476 | V6 | 4 |  | unimplemented | RW
40477 | VAr6 | 4 |  | unimplemented | RW
40478 | V7 | 4 |  | unimplemented | RW
40479 | VAr7 | 4 |  | unimplemented | RW
40480 | V8 | 4 |  | unimplemented | RW
40481 | VAr8 | 4 |  | unimplemented | RW
40482 | V9 | 4 |  | unimplemented | RW
40483 | VAr9 | 4 |  | unimplemented | RW
40484 | V10 | 4 |  | unimplemented | RW
40485 | VAr10 | 4 |  | unimplemented | RW
40486 | V11 | 4 |  | unimplemented | RW
40487 | VAr11 | 4 |  | unimplemented | RW
40488 | V12 | 4 |  | unimplemented | RW
40489 | VAr12 | 4 |  | unimplemented | RW
40490 | V13 | 4 |  | unimplemented | RW
40491 | VAr13 | 4 |  | unimplemented | RW
40492 | V14 | 4 |  | unimplemented | RW
40493 | VAr14 | 4 |  | unimplemented | RW
40494 | V15 | 4 |  | unimplemented | RW
40495 | VAr15 | 4 |  | unimplemented | RW
40496 | V16 | 4 |  | unimplemented | RW
40497 | VAr16 | 4 |  | unimplemented | RW
40498 | V17 | 4 |  | unimplemented | RW
40499 | VAr17 | 4 |  | unimplemented | RW
40500 | V18 | 4 |  | unimplemented | RW
40501 | VAr18 | 4 |  | unimplemented | RW
40502 | V19 | 4 |  | unimplemented | RW
40503 | VAr19 | 4 |  | unimplemented | RW
40504 | V20 | 4 |  | unimplemented | RW
40505 | VAr20 | 4 |  | unimplemented | RW
40506 | CrvNam | 4 |  | unimplemented | RW
40514 | RmpTms | 4 |  | unimplemented | RW
40515 | RmpDecTmm | 4 |  | unimplemented | RW
40516 | RmpIncTmm | 4 |  | unimplemented | RW
40517 | ReadOnly | 4 |  | supported | R

## 129
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40518 | ID |  |  | 129
40519 | L |  |  | 210
40520 | ActCrv |  |  | supported | RW
40521 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40522 | WinTms |  |  | unimplemented | RW
40523 | RvrtTms |  |  | unimplemented | RW
40524 | RmpTms |  |  | unimplemented | RW
40525 | NCrv |  |  | supported | R
40526 | NPt |  |  | supported | R
40527 | Tms_SF |  |  | -2 | R
40528 | V_SF |  |  | -1 | R
40529 | Pad |  |  |  | R
40530 | ActPt | 1 |  | supported | RW
40531 | Tms1 | 1 |  | supported | RW
40532 | V1 | 1 |  | supported | RW
40533 | Tms2 | 1 |  | supported | RW
40534 | V2 | 1 |  | supported | RW
40535 | Tms3 | 1 |  | supported | RW
40536 | V3 | 1 |  | supported | RW
40537 | Tms4 | 1 |  | supported | RW
40538 | V4 | 1 |  | supported | RW
40539 | Tms5 | 1 |  | supported | RW
40540 | V5 | 1 |  | supported | RW
40541 | Tms6 | 1 |  | supported | RW
40542 | V6 | 1 |  | supported | RW
40543 | Tms7 | 1 |  | supported | RW
40544 | V7 | 1 |  | supported | RW
40545 | Tms8 | 1 |  | supported | RW
40546 | V8 | 1 |  | supported | RW
40547 | Tms9 | 1 |  | supported | RW
40548 | V9 | 1 |  | supported | RW
40549 | Tms10 | 1 |  | supported | RW
40550 | V10 | 1 |  | supported | RW
40551 | Tms11 | 1 |  | unimplemented | RW
40552 | V11 | 1 |  | unimplemented | RW
40553 | Tms12 | 1 |  | unimplemented | RW
40554 | V12 | 1 |  | unimplemented | RW
40555 | Tms13 | 1 |  | unimplemented | RW
40556 | V13 | 1 |  | unimplemented | RW
40557 | Tms14 | 1 |  | unimplemented | RW
40558 | V14 | 1 |  | unimplemented | RW
40559 | Tms15 | 1 |  | unimplemented | RW
40560 | V15 | 1 |  | unimplemented | RW
40561 | Tms16 | 1 |  | unimplemented | RW
40562 | V16 | 1 |  | unimplemented | RW
40563 | Tms17 | 1 |  | unimplemented | RW
40564 | V17 | 1 |  | unimplemented | RW
40565 | Tms18 | 1 |  | unimplemented | RW
40566 | V18 | 1 |  | unimplemented | RW
40567 | Tms19 | 1 |  | unimplemented | RW
40568 | V19 | 1 |  | unimplemented | RW
40569 | Tms20 | 1 |  | unimplemented | RW
40570 | V20 | 1 |  | unimplemented | RW
40571 | CrvNam | 1 |  | unimplemented | RW
40579 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
40580 | ActPt | 2 |  | supported | RW
40581 | Tms1 | 2 |  | supported | RW
40582 | V1 | 2 |  | supported | RW
40583 | Tms2 | 2 |  | supported | RW
40584 | V2 | 2 |  | supported | RW
40585 | Tms3 | 2 |  | supported | RW
40586 | V3 | 2 |  | supported | RW
40587 | Tms4 | 2 |  | supported | RW
40588 | V4 | 2 |  | supported | RW
40589 | Tms5 | 2 |  | supported | RW
40590 | V5 | 2 |  | supported | RW
40591 | Tms6 | 2 |  | supported | RW
40592 | V6 | 2 |  | supported | RW
40593 | Tms7 | 2 |  | supported | RW
40594 | V7 | 2 |  | supported | RW
40595 | Tms8 | 2 |  | supported | RW
40596 | V8 | 2 |  | supported | RW
40597 | Tms9 | 2 |  | supported | RW
40598 | V9 | 2 |  | supported | RW
40599 | Tms10 | 2 |  | supported | RW
40600 | V10 | 2 |  | supported | RW
40601 | Tms11 | 2 |  | unimplemented | RW
40602 | V11 | 2 |  | unimplemented | RW
40603 | Tms12 | 2 |  | unimplemented | RW
40604 | V12 | 2 |  | unimplemented | RW
40605 | Tms13 | 2 |  | unimplemented | RW
40606 | V13 | 2 |  | unimplemented | RW
40607 | Tms14 | 2 |  | unimplemented | RW
40608 | V14 | 2 |  | unimplemented | RW
40609 | Tms15 | 2 |  | unimplemented | RW
40610 | V15 | 2 |  | unimplemented | RW
40611 | Tms16 | 2 |  | unimplemented | RW
40612 | V16 | 2 |  | unimplemented | RW
40613 | Tms17 | 2 |  | unimplemented | RW
40614 | V17 | 2 |  | unimplemented | RW
40615 | Tms18 | 2 |  | unimplemented | RW
40616 | V18 | 2 |  | unimplemented | RW
40617 | Tms19 | 2 |  | unimplemented | RW
40618 | V19 | 2 |  | unimplemented | RW
40619 | Tms20 | 2 |  | unimplemented | RW
40620 | V20 | 2 |  | unimplemented | RW
40621 | CrvNam | 2 |  | unimplemented | RW
40629 | ReadOnly | 2 |  | supported | R
40630 | ActPt | 3 |  | supported | RW
40631 | Tms1 | 3 |  | supported | RW
40632 | V1 | 3 |  | supported | RW
40633 | Tms2 | 3 |  | supported | RW
40634 | V2 | 3 |  | supported | RW
40635 | Tms3 | 3 |  | supported | RW
40636 | V3 | 3 |  | supported | RW
40637 | Tms4 | 3 |  | supported | RW
40638 | V4 | 3 |  | supported | RW
40639 | Tms5 | 3 |  | supported | RW
40640 | V5 | 3 |  | supported | RW
40641 | Tms6 | 3 |  | supported | RW
40642 | V6 | 3 |  | supported | RW
40643 | Tms7 | 3 |  | supported | RW
40644 | V7 | 3 |  | supported | RW
40645 | Tms8 | 3 |  | supported | RW
40646 | V8 | 3 |  | supported | RW
40647 | Tms9 | 3 |  | supported | RW
40648 | V9 | 3 |  | supported | RW
40649 | Tms10 | 3 |  | supported | RW
40650 | V10 | 3 |  | supported | RW
40651 | Tms11 | 3 |  | unimplemented | RW
40652 | V11 | 3 |  | unimplemented | RW
40653 | Tms12 | 3 |  | unimplemented | RW
40654 | V12 | 3 |  | unimplemented | RW
40655 | Tms13 | 3 |  | unimplemented | RW
40656 | V13 | 3 |  | unimplemented | RW
40657 | Tms14 | 3 |  | unimplemented | RW
40658 | V14 | 3 |  | unimplemented | RW
40659 | Tms15 | 3 |  | unimplemented | RW
40660 | V15 | 3 |  | unimplemented | RW
40661 | Tms16 | 3 |  | unimplemented | RW
40662 | V16 | 3 |  | unimplemented | RW
40663 | Tms17 | 3 |  | unimplemented | RW
40664 | V17 | 3 |  | unimplemented | RW
40665 | Tms18 | 3 |  | unimplemented | RW
40666 | V18 | 3 |  | unimplemented | RW
40667 | Tms19 | 3 |  | unimplemented | RW
40668 | V19 | 3 |  | unimplemented | RW
40669 | Tms20 | 3 |  | unimplemented | RW
40670 | V20 | 3 |  | unimplemented | RW
40671 | CrvNam | 3 |  | unimplemented | RW
40679 | ReadOnly | 3 |  | supported | R
40680 | ActPt | 4 |  | supported | RW
40681 | Tms1 | 4 |  | supported | RW
40682 | V1 | 4 |  | supported | RW
40683 | Tms2 | 4 |  | supported | RW
40684 | V2 | 4 |  | supported | RW
40685 | Tms3 | 4 |  | supported | RW
40686 | V3 | 4 |  | supported | RW
40687 | Tms4 | 4 |  | supported | RW
40688 | V4 | 4 |  | supported | RW
40689 | Tms5 | 4 |  | supported | RW
40690 | V5 | 4 |  | supported | RW
40691 | Tms6 | 4 |  | supported | RW
40692 | V6 | 4 |  | supported | RW
40693 | Tms7 | 4 |  | supported | RW
40694 | V7 | 4 |  | supported | RW
40695 | Tms8 | 4 |  | supported | RW
40696 | V8 | 4 |  | supported | RW
40697 | Tms9 | 4 |  | supported | RW
40698 | V9 | 4 |  | supported | RW
40699 | Tms10 | 4 |  | supported | RW
40700 | V10 | 4 |  | supported | RW
40701 | Tms11 | 4 |  | unimplemented | RW
40702 | V11 | 4 |  | unimplemented | RW
40703 | Tms12 | 4 |  | unimplemented | RW
40704 | V12 | 4 |  | unimplemented | RW
40705 | Tms13 | 4 |  | unimplemented | RW
40706 | V13 | 4 |  | unimplemented | RW
40707 | Tms14 | 4 |  | unimplemented | RW
40708 | V14 | 4 |  | unimplemented | RW
40709 | Tms15 | 4 |  | unimplemented | RW
40710 | V15 | 4 |  | unimplemented | RW
40711 | Tms16 | 4 |  | unimplemented | RW
40712 | V16 | 4 |  | unimplemented | RW
40713 | Tms17 | 4 |  | unimplemented | RW
40714 | V17 | 4 |  | unimplemented | RW
40715 | Tms18 | 4 |  | unimplemented | RW
40716 | V18 | 4 |  | unimplemented | RW
40717 | Tms19 | 4 |  | unimplemented | RW
40718 | V19 | 4 |  | unimplemented | RW
40719 | Tms20 | 4 |  | unimplemented | RW
40720 | V20 | 4 |  | unimplemented | RW
40721 | CrvNam | 4 |  | unimplemented | RW
40729 | ReadOnly | 4 |  | supported | R

## 130
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40730 | ID |  |  | 130
40731 | L |  |  | 210
40732 | ActCrv |  |  | supported | RW
40733 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40734 | WinTms |  |  | unimplemented | RW
40735 | RvrtTms |  |  | unimplemented | RW
40736 | RmpTms |  |  | unimplemented | RW
40737 | NCrv |  |  | supported | R
40738 | NPt |  |  | supported | R
40739 | Tms_SF |  |  | -2 | R
40740 | V_SF |  |  | -1 | R
40741 | Pad |  |  |  | R
40742 | ActPt | 1 |  | supported | RW
40743 | Tms1 | 1 |  | supported | RW
40744 | V1 | 1 |  | supported | RW
40745 | Tms2 | 1 |  | supported | RW
40746 | V2 | 1 |  | supported | RW
40747 | Tms3 | 1 |  | supported | RW
40748 | V3 | 1 |  | supported | RW
40749 | Tms4 | 1 |  | supported | RW
40750 | V4 | 1 |  | supported | RW
40751 | Tms5 | 1 |  | supported | RW
40752 | V5 | 1 |  | supported | RW
40753 | Tms6 | 1 |  | supported | RW
40754 | V6 | 1 |  | supported | RW
40755 | Tms7 | 1 |  | supported | RW
40756 | V7 | 1 |  | supported | RW
40757 | Tms8 | 1 |  | supported | RW
40758 | V8 | 1 |  | supported | RW
40759 | Tms9 | 1 |  | supported | RW
40760 | V9 | 1 |  | supported | RW
40761 | Tms10 | 1 |  | supported | RW
40762 | V10 | 1 |  | supported | RW
40763 | Tms11 | 1 |  | unimplemented | RW
40764 | V11 | 1 |  | unimplemented | RW
40765 | Tms12 | 1 |  | unimplemented | RW
40766 | V12 | 1 |  | unimplemented | RW
40767 | Tms13 | 1 |  | unimplemented | RW
40768 | V13 | 1 |  | unimplemented | RW
40769 | Tms14 | 1 |  | unimplemented | RW
40770 | V14 | 1 |  | unimplemented | RW
40771 | Tms15 | 1 |  | unimplemented | RW
40772 | V15 | 1 |  | unimplemented | RW
40773 | Tms16 | 1 |  | unimplemented | RW
40774 | V16 | 1 |  | unimplemented | RW
40775 | Tms17 | 1 |  | unimplemented | RW
40776 | V17 | 1 |  | unimplemented | RW
40777 | Tms18 | 1 |  | unimplemented | RW
40778 | V18 | 1 |  | unimplemented | RW
40779 | Tms19 | 1 |  | unimplemented | RW
40780 | V19 | 1 |  | unimplemented | RW
40781 | Tms20 | 1 |  | unimplemented | RW
40782 | V20 | 1 |  | unimplemented | RW
40783 | CrvNam | 1 |  | unimplemented | RW
40791 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
40792 | ActPt | 2 |  | supported | RW
40793 | Tms1 | 2 |  | supported | RW
40794 | V1 | 2 |  | supported | RW
40795 | Tms2 | 2 |  | supported | RW
40796 | V2 | 2 |  | supported | RW
40797 | Tms3 | 2 |  | supported | RW
40798 | V3 | 2 |  | supported | RW
40799 | Tms4 | 2 |  | supported | RW
40800 | V4 | 2 |  | supported | RW
40801 | Tms5 | 2 |  | supported | RW
40802 | V5 | 2 |  | supported | RW
40803 | Tms6 | 2 |  | supported | RW
40804 | V6 | 2 |  | supported | RW
40805 | Tms7 | 2 |  | supported | RW
40806 | V7 | 2 |  | supported | RW
40807 | Tms8 | 2 |  | supported | RW
40808 | V8 | 2 |  | supported | RW
40809 | Tms9 | 2 |  | supported | RW
40810 | V9 | 2 |  | supported | RW
40811 | Tms10 | 2 |  | supported | RW
40812 | V10 | 2 |  | supported | RW
40813 | Tms11 | 2 |  | unimplemented | RW
40814 | V11 | 2 |  | unimplemented | RW
40815 | Tms12 | 2 |  | unimplemented | RW
40816 | V12 | 2 |  | unimplemented | RW
40817 | Tms13 | 2 |  | unimplemented | RW
40818 | V13 | 2 |  | unimplemented | RW
40819 | Tms14 | 2 |  | unimplemented | RW
40820 | V14 | 2 |  | unimplemented | RW
40821 | Tms15 | 2 |  | unimplemented | RW
40822 | V15 | 2 |  | unimplemented | RW
40823 | Tms16 | 2 |  | unimplemented | RW
40824 | V16 | 2 |  | unimplemented | RW
40825 | Tms17 | 2 |  | unimplemented | RW
40826 | V17 | 2 |  | unimplemented | RW
40827 | Tms18 | 2 |  | unimplemented | RW
40828 | V18 | 2 |  | unimplemented | RW
40829 | Tms19 | 2 |  | unimplemented | RW
40830 | V19 | 2 |  | unimplemented | RW
40831 | Tms20 | 2 |  | unimplemented | RW
40832 | V20 | 2 |  | unimplemented | RW
40833 | CrvNam | 2 |  | unimplemented | RW
40841 | ReadOnly | 2 |  | supported | R
40842 | ActPt | 3 |  | supported | RW
40843 | Tms1 | 3 |  | supported | RW
40844 | V1 | 3 |  | supported | RW
40845 | Tms2 | 3 |  | supported | RW
40846 | V2 | 3 |  | supported | RW
40847 | Tms3 | 3 |  | supported | RW
40848 | V3 | 3 |  | supported | RW
40849 | Tms4 | 3 |  | supported | RW
40850 | V4 | 3 |  | supported | RW
40851 | Tms5 | 3 |  | supported | RW
40852 | V5 | 3 |  | supported | RW
40853 | Tms6 | 3 |  | supported | RW
40854 | V6 | 3 |  | supported | RW
40855 | Tms7 | 3 |  | supported | RW
40856 | V7 | 3 |  | supported | RW
40857 | Tms8 | 3 |  | supported | RW
40858 | V8 | 3 |  | supported | RW
40859 | Tms9 | 3 |  | supported | RW
40860 | V9 | 3 |  | supported | RW
40861 | Tms10 | 3 |  | supported | RW
40862 | V10 | 3 |  | supported | RW
40863 | Tms11 | 3 |  | unimplemented | RW
40864 | V11 | 3 |  | unimplemented | RW
40865 | Tms12 | 3 |  | unimplemented | RW
40866 | V12 | 3 |  | unimplemented | RW
40867 | Tms13 | 3 |  | unimplemented | RW
40868 | V13 | 3 |  | unimplemented | RW
40869 | Tms14 | 3 |  | unimplemented | RW
40870 | V14 | 3 |  | unimplemented | RW
40871 | Tms15 | 3 |  | unimplemented | RW
40872 | V15 | 3 |  | unimplemented | RW
40873 | Tms16 | 3 |  | unimplemented | RW
40874 | V16 | 3 |  | unimplemented | RW
40875 | Tms17 | 3 |  | unimplemented | RW
40876 | V17 | 3 |  | unimplemented | RW
40877 | Tms18 | 3 |  | unimplemented | RW
40878 | V18 | 3 |  | unimplemented | RW
40879 | Tms19 | 3 |  | unimplemented | RW
40880 | V19 | 3 |  | unimplemented | RW
40881 | Tms20 | 3 |  | unimplemented | RW
40882 | V20 | 3 |  | unimplemented | RW
40883 | CrvNam | 3 |  | unimplemented | RW
40891 | ReadOnly | 3 |  | supported | R
40892 | ActPt | 4 |  | supported | RW
40893 | Tms1 | 4 |  | supported | RW
40894 | V1 | 4 |  | supported | RW
40895 | Tms2 | 4 |  | supported | RW
40896 | V2 | 4 |  | supported | RW
40897 | Tms3 | 4 |  | supported | RW
40898 | V3 | 4 |  | supported | RW
40899 | Tms4 | 4 |  | supported | RW
40900 | V4 | 4 |  | supported | RW
40901 | Tms5 | 4 |  | supported | RW
40902 | V5 | 4 |  | supported | RW
40903 | Tms6 | 4 |  | supported | RW
40904 | V6 | 4 |  | supported | RW
40905 | Tms7 | 4 |  | supported | RW
40906 | V7 | 4 |  | supported | RW
40907 | Tms8 | 4 |  | supported | RW
40908 | V8 | 4 |  | supported | RW
40909 | Tms9 | 4 |  | supported | RW
40910 | V9 | 4 |  | supported | RW
40911 | Tms10 | 4 |  | supported | RW
40912 | V10 | 4 |  | supported | RW
40913 | Tms11 | 4 |  | unimplemented | RW
40914 | V11 | 4 |  | unimplemented | RW
40915 | Tms12 | 4 |  | unimplemented | RW
40916 | V12 | 4 |  | unimplemented | RW
40917 | Tms13 | 4 |  | unimplemented | RW
40918 | V13 | 4 |  | unimplemented | RW
40919 | Tms14 | 4 |  | unimplemented | RW
40920 | V14 | 4 |  | unimplemented | RW
40921 | Tms15 | 4 |  | unimplemented | RW
40922 | V15 | 4 |  | unimplemented | RW
40923 | Tms16 | 4 |  | unimplemented | RW
40924 | V16 | 4 |  | unimplemented | RW
40925 | Tms17 | 4 |  | unimplemented | RW
40926 | V17 | 4 |  | unimplemented | RW
40927 | Tms18 | 4 |  | unimplemented | RW
40928 | V18 | 4 |  | unimplemented | RW
40929 | Tms19 | 4 |  | unimplemented | RW
40930 | V19 | 4 |  | unimplemented | RW
40931 | Tms20 | 4 |  | unimplemented | RW
40932 | V20 | 4 |  | unimplemented | RW
40933 | CrvNam | 4 |  | unimplemented | RW
40941 | ReadOnly | 4 |  | supported | R

## 64254
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
40942 | ID |  |  | 64254
40943 | L |  |  | 370
40944 | ActCrv |  |  | supported | RW
40945 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
40946 | WinTms |  |  | unimplemented | RW
40947 | RvrtTms |  |  | unimplemented | RW
40948 | RmpTms |  |  | unimplemented | RW
40949 | NCrv |  |  | supported | R
40950 | NPt |  |  | supported | R
40951 | Tms_SF |  |  | -6 | R
40952 | V_SF |  |  | -1 | R
40953 | Pad |  |  |  | R
40954 | ActPt | 1 |  | supported | RW
40955 | Tms1 | 1 |  | supported | RW
40957 | V1 | 1 |  | supported | RW
40958 | Fn1 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40959 | Tms2 | 1 |  | supported | RW
40961 | V2 | 1 |  | supported | RW
40962 | Fn2 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40963 | Tms3 | 1 |  | supported | RW
40965 | V3 | 1 |  | supported | RW
40966 | Fn3 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40967 | Tms4 | 1 |  | supported | RW
40969 | V4 | 1 |  | supported | RW
40970 | Fn4 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40971 | Tms5 | 1 |  | supported | RW
40973 | V5 | 1 |  | supported | RW
40974 | Fn5 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40975 | Tms6 | 1 |  | supported | RW
40977 | V6 | 1 |  | supported | RW
40978 | Fn6 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40979 | Tms7 | 1 |  | supported | RW
40981 | V7 | 1 |  | supported | RW
40982 | Fn7 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40983 | Tms8 | 1 |  | supported | RW
40985 | V8 | 1 |  | supported | RW
40986 | Fn8 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40987 | Tms9 | 1 |  | supported | RW
40989 | V9 | 1 |  | supported | RW
40990 | Fn9 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40991 | Tms10 | 1 |  | supported | RW
40993 | V10 | 1 |  | supported | RW
40994 | Fn10 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
40995 | Tms11 | 1 |  | unimplemented | RW
40997 | V11 | 1 |  | unimplemented | RW
40998 | Fn11 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
40999 | Tms12 | 1 |  | unimplemented | RW
41001 | V12 | 1 |  | unimplemented | RW
41002 | Fn12 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41003 | Tms13 | 1 |  | unimplemented | RW
41005 | V13 | 1 |  | unimplemented | RW
41006 | Fn13 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41007 | Tms14 | 1 |  | unimplemented | RW
41009 | V14 | 1 |  | unimplemented | RW
41010 | Fn14 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41011 | Tms15 | 1 |  | unimplemented | RW
41013 | V15 | 1 |  | unimplemented | RW
41014 | Fn15 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41015 | Tms16 | 1 |  | unimplemented | RW
41017 | V16 | 1 |  | unimplemented | RW
41018 | Fn16 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41019 | Tms17 | 1 |  | unimplemented | RW
41021 | V17 | 1 |  | unimplemented | RW
41022 | Fn17 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41023 | Tms18 | 1 |  | unimplemented | RW
41025 | V18 | 1 |  | unimplemented | RW
41026 | Fn18 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41027 | Tms19 | 1 |  | unimplemented | RW
41029 | V19 | 1 |  | unimplemented | RW
41030 | Fn19 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41031 | Tms20 | 1 |  | unimplemented | RW
41033 | V20 | 1 |  | unimplemented | RW
41034 | Fn20 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41035 | CrvNam | 1 |  | unimplemented | RW
41043 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
41044 | ActPt | 2 |  | supported | RW
41045 | Tms1 | 2 |  | supported | RW
41047 | V1 | 2 |  | supported | RW
41048 | Fn1 | 2 |  | supported | RW
41049 | Tms2 | 2 |  | supported | RW
41051 | V2 | 2 |  | supported | RW
41052 | Fn2 | 2 |  | supported | RW
41053 | Tms3 | 2 |  | supported | RW
41055 | V3 | 2 |  | supported | RW
41056 | Fn3 | 2 |  | supported | RW
41057 | Tms4 | 2 |  | supported | RW
41059 | V4 | 2 |  | supported | RW
41060 | Fn4 | 2 |  | supported | RW
41061 | Tms5 | 2 |  | supported | RW
41063 | V5 | 2 |  | supported | RW
41064 | Fn5 | 2 |  | supported | RW
41065 | Tms6 | 2 |  | supported | RW
41067 | V6 | 2 |  | supported | RW
41068 | Fn6 | 2 |  | supported | RW
41069 | Tms7 | 2 |  | supported | RW
41071 | V7 | 2 |  | supported | RW
41072 | Fn7 | 2 |  | supported | RW
41073 | Tms8 | 2 |  | supported | RW
41075 | V8 | 2 |  | supported | RW
41076 | Fn8 | 2 |  | supported | RW
41077 | Tms9 | 2 |  | supported | RW
41079 | V9 | 2 |  | supported | RW
41080 | Fn9 | 2 |  | supported | RW
41081 | Tms10 | 2 |  | supported | RW
41083 | V10 | 2 |  | supported | RW
41084 | Fn10 | 2 |  | supported | RW
41085 | Tms11 | 2 |  | unimplemented | RW
41087 | V11 | 2 |  | unimplemented | RW
41088 | Fn11 | 2 |  | unimplemented | RW
41089 | Tms12 | 2 |  | unimplemented | RW
41091 | V12 | 2 |  | unimplemented | RW
41092 | Fn12 | 2 |  | unimplemented | RW
41093 | Tms13 | 2 |  | unimplemented | RW
41095 | V13 | 2 |  | unimplemented | RW
41096 | Fn13 | 2 |  | unimplemented | RW
41097 | Tms14 | 2 |  | unimplemented | RW
41099 | V14 | 2 |  | unimplemented | RW
41100 | Fn14 | 2 |  | unimplemented | RW
41101 | Tms15 | 2 |  | unimplemented | RW
41103 | V15 | 2 |  | unimplemented | RW
41104 | Fn15 | 2 |  | unimplemented | RW
41105 | Tms16 | 2 |  | unimplemented | RW
41107 | V16 | 2 |  | unimplemented | RW
41108 | Fn16 | 2 |  | unimplemented | RW
41109 | Tms17 | 2 |  | unimplemented | RW
41111 | V17 | 2 |  | unimplemented | RW
41112 | Fn17 | 2 |  | unimplemented | RW
41113 | Tms18 | 2 |  | unimplemented | RW
41115 | V18 | 2 |  | unimplemented | RW
41116 | Fn18 | 2 |  | unimplemented | RW
41117 | Tms19 | 2 |  | unimplemented | RW
41119 | V19 | 2 |  | unimplemented | RW
41120 | Fn19 | 2 |  | unimplemented | RW
41121 | Tms20 | 2 |  | unimplemented | RW
41123 | V20 | 2 |  | unimplemented | RW
41124 | Fn20 | 2 |  | unimplemented | RW
41125 | CrvNam | 2 |  | unimplemented | RW
41133 | ReadOnly | 2 |  | supported | R
41134 | ActPt | 3 |  | supported | RW
41135 | Tms1 | 3 |  | supported | RW
41137 | V1 | 3 |  | supported | RW
41138 | Fn1 | 3 |  | supported | RW
41139 | Tms2 | 3 |  | supported | RW
41141 | V2 | 3 |  | supported | RW
41142 | Fn2 | 3 |  | supported | RW
41143 | Tms3 | 3 |  | supported | RW
41145 | V3 | 3 |  | supported | RW
41146 | Fn3 | 3 |  | supported | RW
41147 | Tms4 | 3 |  | supported | RW
41149 | V4 | 3 |  | supported | RW
41150 | Fn4 | 3 |  | supported | RW
41151 | Tms5 | 3 |  | supported | RW
41153 | V5 | 3 |  | supported | RW
41154 | Fn5 | 3 |  | supported | RW
41155 | Tms6 | 3 |  | supported | RW
41157 | V6 | 3 |  | supported | RW
41158 | Fn6 | 3 |  | supported | RW
41159 | Tms7 | 3 |  | supported | RW
41161 | V7 | 3 |  | supported | RW
41162 | Fn7 | 3 |  | supported | RW
41163 | Tms8 | 3 |  | supported | RW
41165 | V8 | 3 |  | supported | RW
41166 | Fn8 | 3 |  | supported | RW
41167 | Tms9 | 3 |  | supported | RW
41169 | V9 | 3 |  | supported | RW
41170 | Fn9 | 3 |  | supported | RW
41171 | Tms10 | 3 |  | supported | RW
41173 | V10 | 3 |  | supported | RW
41174 | Fn10 | 3 |  | supported | RW
41175 | Tms11 | 3 |  | unimplemented | RW
41177 | V11 | 3 |  | unimplemented | RW
41178 | Fn11 | 3 |  | unimplemented | RW
41179 | Tms12 | 3 |  | unimplemented | RW
41181 | V12 | 3 |  | unimplemented | RW
41182 | Fn12 | 3 |  | unimplemented | RW
41183 | Tms13 | 3 |  | unimplemented | RW
41185 | V13 | 3 |  | unimplemented | RW
41186 | Fn13 | 3 |  | unimplemented | RW
41187 | Tms14 | 3 |  | unimplemented | RW
41189 | V14 | 3 |  | unimplemented | RW
41190 | Fn14 | 3 |  | unimplemented | RW
41191 | Tms15 | 3 |  | unimplemented | RW
41193 | V15 | 3 |  | unimplemented | RW
41194 | Fn15 | 3 |  | unimplemented | RW
41195 | Tms16 | 3 |  | unimplemented | RW
41197 | V16 | 3 |  | unimplemented | RW
41198 | Fn16 | 3 |  | unimplemented | RW
41199 | Tms17 | 3 |  | unimplemented | RW
41201 | V17 | 3 |  | unimplemented | RW
41202 | Fn17 | 3 |  | unimplemented | RW
41203 | Tms18 | 3 |  | unimplemented | RW
41205 | V18 | 3 |  | unimplemented | RW
41206 | Fn18 | 3 |  | unimplemented | RW
41207 | Tms19 | 3 |  | unimplemented | RW
41209 | V19 | 3 |  | unimplemented | RW
41210 | Fn19 | 3 |  | unimplemented | RW
41211 | Tms20 | 3 |  | unimplemented | RW
41213 | V20 | 3 |  | unimplemented | RW
41214 | Fn20 | 3 |  | unimplemented | RW
41215 | CrvNam | 3 |  | unimplemented | RW
41223 | ReadOnly | 3 |  | supported | R
41224 | ActPt | 4 |  | supported | RW
41225 | Tms1 | 4 |  | supported | RW
41227 | V1 | 4 |  | supported | RW
41228 | Fn1 | 4 |  | supported | RW
41229 | Tms2 | 4 |  | supported | RW
41231 | V2 | 4 |  | supported | RW
41232 | Fn2 | 4 |  | supported | RW
41233 | Tms3 | 4 |  | supported | RW
41235 | V3 | 4 |  | supported | RW
41236 | Fn3 | 4 |  | supported | RW
41237 | Tms4 | 4 |  | supported | RW
41239 | V4 | 4 |  | supported | RW
41240 | Fn4 | 4 |  | supported | RW
41241 | Tms5 | 4 |  | supported | RW
41243 | V5 | 4 |  | supported | RW
41244 | Fn5 | 4 |  | supported | RW
41245 | Tms6 | 4 |  | supported | RW
41247 | V6 | 4 |  | supported | RW
41248 | Fn6 | 4 |  | supported | RW
41249 | Tms7 | 4 |  | supported | RW
41251 | V7 | 4 |  | supported | RW
41252 | Fn7 | 4 |  | supported | RW
41253 | Tms8 | 4 |  | supported | RW
41255 | V8 | 4 |  | supported | RW
41256 | Fn8 | 4 |  | supported | RW
41257 | Tms9 | 4 |  | supported | RW
41259 | V9 | 4 |  | supported | RW
41260 | Fn9 | 4 |  | supported | RW
41261 | Tms10 | 4 |  | supported | RW
41263 | V10 | 4 |  | supported | RW
41264 | Fn10 | 4 |  | supported | RW
41265 | Tms11 | 4 |  | unimplemented | RW
41267 | V11 | 4 |  | unimplemented | RW
41268 | Fn11 | 4 |  | unimplemented | RW
41269 | Tms12 | 4 |  | unimplemented | RW
41271 | V12 | 4 |  | unimplemented | RW
41272 | Fn12 | 4 |  | unimplemented | RW
41273 | Tms13 | 4 |  | unimplemented | RW
41275 | V13 | 4 |  | unimplemented | RW
41276 | Fn13 | 4 |  | unimplemented | RW
41277 | Tms14 | 4 |  | unimplemented | RW
41279 | V14 | 4 |  | unimplemented | RW
41280 | Fn14 | 4 |  | unimplemented | RW
41281 | Tms15 | 4 |  | unimplemented | RW
41283 | V15 | 4 |  | unimplemented | RW
41284 | Fn15 | 4 |  | unimplemented | RW
41285 | Tms16 | 4 |  | unimplemented | RW
41287 | V16 | 4 |  | unimplemented | RW
41288 | Fn16 | 4 |  | unimplemented | RW
41289 | Tms17 | 4 |  | unimplemented | RW
41291 | V17 | 4 |  | unimplemented | RW
41292 | Fn17 | 4 |  | unimplemented | RW
41293 | Tms18 | 4 |  | unimplemented | RW
41295 | V18 | 4 |  | unimplemented | RW
41296 | Fn18 | 4 |  | unimplemented | RW
41297 | Tms19 | 4 |  | unimplemented | RW
41299 | V19 | 4 |  | unimplemented | RW
41300 | Fn19 | 4 |  | unimplemented | RW
41301 | Tms20 | 4 |  | unimplemented | RW
41303 | V20 | 4 |  | unimplemented | RW
41304 | Fn20 | 4 |  | unimplemented | RW
41305 | CrvNam | 4 |  | unimplemented | RW
41313 | ReadOnly | 4 |  | supported | R

## 64255
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
41314 | ID |  |  | 64255
41315 | L |  |  | 370
41316 | ActCrv |  |  | supported | RW
41317 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
41318 | WinTms |  |  | unimplemented | RW
41319 | RvrtTms |  |  | unimplemented | RW
41320 | RmpTms |  |  | unimplemented | RW
41321 | NCrv |  |  | supported | R
41322 | NPt |  |  | supported | R
41323 | Tms_SF |  |  | -6 | R
41324 | V_SF |  |  | -1 | R
41325 | Pad |  |  |  | R
41326 | ActPt | 1 |  | supported | RW
41327 | Tms1 | 1 |  | supported | RW
41329 | V1 | 1 |  | supported | RW
41330 | Fn1 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41331 | Tms2 | 1 |  | supported | RW
41333 | V2 | 1 |  | supported | RW
41334 | Fn2 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41335 | Tms3 | 1 |  | supported | RW
41337 | V3 | 1 |  | supported | RW
41338 | Fn3 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41339 | Tms4 | 1 |  | supported | RW
41341 | V4 | 1 |  | supported | RW
41342 | Fn4 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41343 | Tms5 | 1 |  | supported | RW
41345 | V5 | 1 |  | supported | RW
41346 | Fn5 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41347 | Tms6 | 1 |  | supported | RW
41349 | V6 | 1 |  | supported | RW
41350 | Fn6 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41351 | Tms7 | 1 |  | supported | RW
41353 | V7 | 1 |  | supported | RW
41354 | Fn7 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41355 | Tms8 | 1 |  | supported | RW
41357 | V8 | 1 |  | supported | RW
41358 | Fn8 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41359 | Tms9 | 1 |  | supported | RW
41361 | V9 | 1 |  | supported | RW
41362 | Fn9 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41363 | Tms10 | 1 |  | supported | RW
41365 | V10 | 1 |  | supported | RW
41366 | Fn10 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
41367 | Tms11 | 1 |  | unimplemented | RW
41369 | V11 | 1 |  | unimplemented | RW
41370 | Fn11 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41371 | Tms12 | 1 |  | unimplemented | RW
41373 | V12 | 1 |  | unimplemented | RW
41374 | Fn12 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41375 | Tms13 | 1 |  | unimplemented | RW
41377 | V13 | 1 |  | unimplemented | RW
41378 | Fn13 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41379 | Tms14 | 1 |  | unimplemented | RW
41381 | V14 | 1 |  | unimplemented | RW
41382 | Fn14 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41383 | Tms15 | 1 |  | unimplemented | RW
41385 | V15 | 1 |  | unimplemented | RW
41386 | Fn15 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41387 | Tms16 | 1 |  | unimplemented | RW
41389 | V16 | 1 |  | unimplemented | RW
41390 | Fn16 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41391 | Tms17 | 1 |  | unimplemented | RW
41393 | V17 | 1 |  | unimplemented | RW
41394 | Fn17 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41395 | Tms18 | 1 |  | unimplemented | RW
41397 | V18 | 1 |  | unimplemented | RW
41398 | Fn18 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41399 | Tms19 | 1 |  | unimplemented | RW
41401 | V19 | 1 |  | unimplemented | RW
41402 | Fn19 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41403 | Tms20 | 1 |  | unimplemented | RW
41405 | V20 | 1 |  | unimplemented | RW
41406 | Fn20 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
41407 | CrvNam | 1 |  | unimplemented | RW
41415 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
41416 | ActPt | 2 |  | supported | RW
41417 | Tms1 | 2 |  | supported | RW
41419 | V1 | 2 |  | supported | RW
41420 | Fn1 | 2 |  | supported | RW
41421 | Tms2 | 2 |  | supported | RW
41423 | V2 | 2 |  | supported | RW
41424 | Fn2 | 2 |  | supported | RW
41425 | Tms3 | 2 |  | supported | RW
41427 | V3 | 2 |  | supported | RW
41428 | Fn3 | 2 |  | supported | RW
41429 | Tms4 | 2 |  | supported | RW
41431 | V4 | 2 |  | supported | RW
41432 | Fn4 | 2 |  | supported | RW
41433 | Tms5 | 2 |  | supported | RW
41435 | V5 | 2 |  | supported | RW
41436 | Fn5 | 2 |  | supported | RW
41437 | Tms6 | 2 |  | supported | RW
41439 | V6 | 2 |  | supported | RW
41440 | Fn6 | 2 |  | supported | RW
41441 | Tms7 | 2 |  | supported | RW
41443 | V7 | 2 |  | supported | RW
41444 | Fn7 | 2 |  | supported | RW
41445 | Tms8 | 2 |  | supported | RW
41447 | V8 | 2 |  | supported | RW
41448 | Fn8 | 2 |  | supported | RW
41449 | Tms9 | 2 |  | supported | RW
41451 | V9 | 2 |  | supported | RW
41452 | Fn9 | 2 |  | supported | RW
41453 | Tms10 | 2 |  | supported | RW
41455 | V10 | 2 |  | supported | RW
41456 | Fn10 | 2 |  | supported | RW
41457 | Tms11 | 2 |  | unimplemented | RW
41459 | V11 | 2 |  | unimplemented | RW
41460 | Fn11 | 2 |  | unimplemented | RW
41461 | Tms12 | 2 |  | unimplemented | RW
41463 | V12 | 2 |  | unimplemented | RW
41464 | Fn12 | 2 |  | unimplemented | RW
41465 | Tms13 | 2 |  | unimplemented | RW
41467 | V13 | 2 |  | unimplemented | RW
41468 | Fn13 | 2 |  | unimplemented | RW
41469 | Tms14 | 2 |  | unimplemented | RW
41471 | V14 | 2 |  | unimplemented | RW
41472 | Fn14 | 2 |  | unimplemented | RW
41473 | Tms15 | 2 |  | unimplemented | RW
41475 | V15 | 2 |  | unimplemented | RW
41476 | Fn15 | 2 |  | unimplemented | RW
41477 | Tms16 | 2 |  | unimplemented | RW
41479 | V16 | 2 |  | unimplemented | RW
41480 | Fn16 | 2 |  | unimplemented | RW
41481 | Tms17 | 2 |  | unimplemented | RW
41483 | V17 | 2 |  | unimplemented | RW
41484 | Fn17 | 2 |  | unimplemented | RW
41485 | Tms18 | 2 |  | unimplemented | RW
41487 | V18 | 2 |  | unimplemented | RW
41488 | Fn18 | 2 |  | unimplemented | RW
41489 | Tms19 | 2 |  | unimplemented | RW
41491 | V19 | 2 |  | unimplemented | RW
41492 | Fn19 | 2 |  | unimplemented | RW
41493 | Tms20 | 2 |  | unimplemented | RW
41495 | V20 | 2 |  | unimplemented | RW
41496 | Fn20 | 2 |  | unimplemented | RW
41497 | CrvNam | 2 |  | unimplemented | RW
41505 | ReadOnly | 2 |  | supported | R
41506 | ActPt | 3 |  | supported | RW
41507 | Tms1 | 3 |  | supported | RW
41509 | V1 | 3 |  | supported | RW
41510 | Fn1 | 3 |  | supported | RW
41511 | Tms2 | 3 |  | supported | RW
41513 | V2 | 3 |  | supported | RW
41514 | Fn2 | 3 |  | supported | RW
41515 | Tms3 | 3 |  | supported | RW
41517 | V3 | 3 |  | supported | RW
41518 | Fn3 | 3 |  | supported | RW
41519 | Tms4 | 3 |  | supported | RW
41521 | V4 | 3 |  | supported | RW
41522 | Fn4 | 3 |  | supported | RW
41523 | Tms5 | 3 |  | supported | RW
41525 | V5 | 3 |  | supported | RW
41526 | Fn5 | 3 |  | supported | RW
41527 | Tms6 | 3 |  | supported | RW
41529 | V6 | 3 |  | supported | RW
41530 | Fn6 | 3 |  | supported | RW
41531 | Tms7 | 3 |  | supported | RW
41533 | V7 | 3 |  | supported | RW
41534 | Fn7 | 3 |  | supported | RW
41535 | Tms8 | 3 |  | supported | RW
41537 | V8 | 3 |  | supported | RW
41538 | Fn8 | 3 |  | supported | RW
41539 | Tms9 | 3 |  | supported | RW
41541 | V9 | 3 |  | supported | RW
41542 | Fn9 | 3 |  | supported | RW
41543 | Tms10 | 3 |  | supported | RW
41545 | V10 | 3 |  | supported | RW
41546 | Fn10 | 3 |  | supported | RW
41547 | Tms11 | 3 |  | unimplemented | RW
41549 | V11 | 3 |  | unimplemented | RW
41550 | Fn11 | 3 |  | unimplemented | RW
41551 | Tms12 | 3 |  | unimplemented | RW
41553 | V12 | 3 |  | unimplemented | RW
41554 | Fn12 | 3 |  | unimplemented | RW
41555 | Tms13 | 3 |  | unimplemented | RW
41557 | V13 | 3 |  | unimplemented | RW
41558 | Fn13 | 3 |  | unimplemented | RW
41559 | Tms14 | 3 |  | unimplemented | RW
41561 | V14 | 3 |  | unimplemented | RW
41562 | Fn14 | 3 |  | unimplemented | RW
41563 | Tms15 | 3 |  | unimplemented | RW
41565 | V15 | 3 |  | unimplemented | RW
41566 | Fn15 | 3 |  | unimplemented | RW
41567 | Tms16 | 3 |  | unimplemented | RW
41569 | V16 | 3 |  | unimplemented | RW
41570 | Fn16 | 3 |  | unimplemented | RW
41571 | Tms17 | 3 |  | unimplemented | RW
41573 | V17 | 3 |  | unimplemented | RW
41574 | Fn17 | 3 |  | unimplemented | RW
41575 | Tms18 | 3 |  | unimplemented | RW
41577 | V18 | 3 |  | unimplemented | RW
41578 | Fn18 | 3 |  | unimplemented | RW
41579 | Tms19 | 3 |  | unimplemented | RW
41581 | V19 | 3 |  | unimplemented | RW
41582 | Fn19 | 3 |  | unimplemented | RW
41583 | Tms20 | 3 |  | unimplemented | RW
41585 | V20 | 3 |  | unimplemented | RW
41586 | Fn20 | 3 |  | unimplemented | RW
41587 | CrvNam | 3 |  | unimplemented | RW
41595 | ReadOnly | 3 |  | supported | R
41596 | ActPt | 4 |  | supported | RW
41597 | Tms1 | 4 |  | supported | RW
41599 | V1 | 4 |  | supported | RW
41600 | Fn1 | 4 |  | supported | RW
41601 | Tms2 | 4 |  | supported | RW
41603 | V2 | 4 |  | supported | RW
41604 | Fn2 | 4 |  | supported | RW
41605 | Tms3 | 4 |  | supported | RW
41607 | V3 | 4 |  | supported | RW
41608 | Fn3 | 4 |  | supported | RW
41609 | Tms4 | 4 |  | supported | RW
41611 | V4 | 4 |  | supported | RW
41612 | Fn4 | 4 |  | supported | RW
41613 | Tms5 | 4 |  | supported | RW
41615 | V5 | 4 |  | supported | RW
41616 | Fn5 | 4 |  | supported | RW
41617 | Tms6 | 4 |  | supported | RW
41619 | V6 | 4 |  | supported | RW
41620 | Fn6 | 4 |  | supported | RW
41621 | Tms7 | 4 |  | supported | RW
41623 | V7 | 4 |  | supported | RW
41624 | Fn7 | 4 |  | supported | RW
41625 | Tms8 | 4 |  | supported | RW
41627 | V8 | 4 |  | supported | RW
41628 | Fn8 | 4 |  | supported | RW
41629 | Tms9 | 4 |  | supported | RW
41631 | V9 | 4 |  | supported | RW
41632 | Fn9 | 4 |  | supported | RW
41633 | Tms10 | 4 |  | supported | RW
41635 | V10 | 4 |  | supported | RW
41636 | Fn10 | 4 |  | supported | RW
41637 | Tms11 | 4 |  | unimplemented | RW
41639 | V11 | 4 |  | unimplemented | RW
41640 | Fn11 | 4 |  | unimplemented | RW
41641 | Tms12 | 4 |  | unimplemented | RW
41643 | V12 | 4 |  | unimplemented | RW
41644 | Fn12 | 4 |  | unimplemented | RW
41645 | Tms13 | 4 |  | unimplemented | RW
41647 | V13 | 4 |  | unimplemented | RW
41648 | Fn13 | 4 |  | unimplemented | RW
41649 | Tms14 | 4 |  | unimplemented | RW
41651 | V14 | 4 |  | unimplemented | RW
41652 | Fn14 | 4 |  | unimplemented | RW
41653 | Tms15 | 4 |  | unimplemented | RW
41655 | V15 | 4 |  | unimplemented | RW
41656 | Fn15 | 4 |  | unimplemented | RW
41657 | Tms16 | 4 |  | unimplemented | RW
41659 | V16 | 4 |  | unimplemented | RW
41660 | Fn16 | 4 |  | unimplemented | RW
41661 | Tms17 | 4 |  | unimplemented | RW
41663 | V17 | 4 |  | unimplemented | RW
41664 | Fn17 | 4 |  | unimplemented | RW
41665 | Tms18 | 4 |  | unimplemented | RW
41667 | V18 | 4 |  | unimplemented | RW
41668 | Fn18 | 4 |  | unimplemented | RW
41669 | Tms19 | 4 |  | unimplemented | RW
41671 | V19 | 4 |  | unimplemented | RW
41672 | Fn19 | 4 |  | unimplemented | RW
41673 | Tms20 | 4 |  | unimplemented | RW
41675 | V20 | 4 |  | unimplemented | RW
41676 | Fn20 | 4 |  | unimplemented | RW
41677 | CrvNam | 4 |  | unimplemented | RW
41685 | ReadOnly | 4 |  | supported | R

## 132
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
41686 | ID |  |  | 132
41687 | L |  |  | 226
41688 | ActCrv |  |  | supported | RW
41689 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
41690 | WinTms |  |  | unimplemented | RW
41691 | RvrtTms |  |  | unimplemented | RW
41692 | RmpTms |  |  | unimplemented | RW
41693 | NCrv |  |  | supported | R
41694 | NPt |  |  | supported | R
41695 | V_SF |  |  | -1 | R
41696 | DeptRef_SF |  |  | -1 | R
41697 | RmpIncDec_SF |  |  | 0 | R
41698 | ActPt | 1 |  | supported | RW
41699 | DeptRef | 1 |  | supported | RW
|  |  | %WMax | supported
|  |  | %WAval | supported
41700 | V1 | 1 |  | supported | RW
41701 | W1 | 1 |  | supported | RW
41702 | V2 | 1 |  | supported | RW
41703 | W2 | 1 |  | supported | RW
41704 | V3 | 1 |  | unimplemented | RW
41705 | W3 | 1 |  | unimplemented | RW
41706 | V4 | 1 |  | unimplemented | RW
41707 | W4 | 1 |  | unimplemented | RW
41708 | V5 | 1 |  | unimplemented | RW
41709 | W5 | 1 |  | unimplemented | RW
41710 | V6 | 1 |  | unimplemented | RW
41711 | W6 | 1 |  | unimplemented | RW
41712 | V7 | 1 |  | unimplemented | RW
41713 | W7 | 1 |  | unimplemented | RW
41714 | V8 | 1 |  | unimplemented | RW
41715 | W8 | 1 |  | unimplemented | RW
41716 | V9 | 1 |  | unimplemented | RW
41717 | W9 | 1 |  | unimplemented | RW
41718 | V10 | 1 |  | unimplemented | RW
41719 | W10 | 1 |  | unimplemented | RW
41720 | V11 | 1 |  | unimplemented | RW
41721 | W11 | 1 |  | unimplemented | RW
41722 | V12 | 1 |  | unimplemented | RW
41723 | W12 | 1 |  | unimplemented | RW
41724 | V13 | 1 |  | unimplemented | RW
41725 | W13 | 1 |  | unimplemented | RW
41726 | V14 | 1 |  | unimplemented | RW
41727 | W14 | 1 |  | unimplemented | RW
41728 | V15 | 1 |  | unimplemented | RW
41729 | W15 | 1 |  | unimplemented | RW
41730 | V16 | 1 |  | unimplemented | RW
41731 | W16 | 1 |  | unimplemented | RW
41732 | V17 | 1 |  | unimplemented | RW
41733 | W17 | 1 |  | unimplemented | RW
41734 | V18 | 1 |  | unimplemented | RW
41735 | W18 | 1 |  | unimplemented | RW
41736 | V19 | 1 |  | unimplemented | RW
41737 | W19 | 1 |  | unimplemented | RW
41738 | V20 | 1 |  | unimplemented | RW
41739 | W20 | 1 |  | unimplemented | RW
41740 | CrvNam | 1 |  | unimplemented | RW
41748 | RmpPt1Tms | 1 |  | unimplemented | RW
41749 | RmpDecTmm | 1 |  | unimplemented | RW
41750 | RmpIncTmm | 1 |  | unimplemented | RW
41751 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
41752 | ActPt | 2 |  | supported | RW
41753 | DeptRef | 2 |  | supported | RW
41754 | V1 | 2 |  | supported | RW
41755 | W1 | 2 |  | supported | RW
41756 | V2 | 2 |  | supported | RW
41757 | W2 | 2 |  | supported | RW
41758 | V3 | 2 |  | unimplemented | RW
41759 | W3 | 2 |  | unimplemented | RW
41760 | V4 | 2 |  | unimplemented | RW
41761 | W4 | 2 |  | unimplemented | RW
41762 | V5 | 2 |  | unimplemented | RW
41763 | W5 | 2 |  | unimplemented | RW
41764 | V6 | 2 |  | unimplemented | RW
41765 | W6 | 2 |  | unimplemented | RW
41766 | V7 | 2 |  | unimplemented | RW
41767 | W7 | 2 |  | unimplemented | RW
41768 | V8 | 2 |  | unimplemented | RW
41769 | W8 | 2 |  | unimplemented | RW
41770 | V9 | 2 |  | unimplemented | RW
41771 | W9 | 2 |  | unimplemented | RW
41772 | V10 | 2 |  | unimplemented | RW
41773 | W10 | 2 |  | unimplemented | RW
41774 | V11 | 2 |  | unimplemented | RW
41775 | W11 | 2 |  | unimplemented | RW
41776 | V12 | 2 |  | unimplemented | RW
41777 | W12 | 2 |  | unimplemented | RW
41778 | V13 | 2 |  | unimplemented | RW
41779 | W13 | 2 |  | unimplemented | RW
41780 | V14 | 2 |  | unimplemented | RW
41781 | W14 | 2 |  | unimplemented | RW
41782 | V15 | 2 |  | unimplemented | RW
41783 | W15 | 2 |  | unimplemented | RW
41784 | V16 | 2 |  | unimplemented | RW
41785 | W16 | 2 |  | unimplemented | RW
41786 | V17 | 2 |  | unimplemented | RW
41787 | W17 | 2 |  | unimplemented | RW
41788 | V18 | 2 |  | unimplemented | RW
41789 | W18 | 2 |  | unimplemented | RW
41790 | V19 | 2 |  | unimplemented | RW
41791 | W19 | 2 |  | unimplemented | RW
41792 | V20 | 2 |  | unimplemented | RW
41793 | W20 | 2 |  | unimplemented | RW
41794 | CrvNam | 2 |  | unimplemented | RW
41802 | RmpPt1Tms | 2 |  | unimplemented | RW
41803 | RmpDecTmm | 2 |  | unimplemented | RW
41804 | RmpIncTmm | 2 |  | unimplemented | RW
41805 | ReadOnly | 2 |  | supported | R
41806 | ActPt | 3 |  | supported | RW
41807 | DeptRef | 3 |  | supported | RW
41808 | V1 | 3 |  | supported | RW
41809 | W1 | 3 |  | supported | RW
41810 | V2 | 3 |  | supported | RW
41811 | W2 | 3 |  | supported | RW
41812 | V3 | 3 |  | unimplemented | RW
41813 | W3 | 3 |  | unimplemented | RW
41814 | V4 | 3 |  | unimplemented | RW
41815 | W4 | 3 |  | unimplemented | RW
41816 | V5 | 3 |  | unimplemented | RW
41817 | W5 | 3 |  | unimplemented | RW
41818 | V6 | 3 |  | unimplemented | RW
41819 | W6 | 3 |  | unimplemented | RW
41820 | V7 | 3 |  | unimplemented | RW
41821 | W7 | 3 |  | unimplemented | RW
41822 | V8 | 3 |  | unimplemented | RW
41823 | W8 | 3 |  | unimplemented | RW
41824 | V9 | 3 |  | unimplemented | RW
41825 | W9 | 3 |  | unimplemented | RW
41826 | V10 | 3 |  | unimplemented | RW
41827 | W10 | 3 |  | unimplemented | RW
41828 | V11 | 3 |  | unimplemented | RW
41829 | W11 | 3 |  | unimplemented | RW
41830 | V12 | 3 |  | unimplemented | RW
41831 | W12 | 3 |  | unimplemented | RW
41832 | V13 | 3 |  | unimplemented | RW
41833 | W13 | 3 |  | unimplemented | RW
41834 | V14 | 3 |  | unimplemented | RW
41835 | W14 | 3 |  | unimplemented | RW
41836 | V15 | 3 |  | unimplemented | RW
41837 | W15 | 3 |  | unimplemented | RW
41838 | V16 | 3 |  | unimplemented | RW
41839 | W16 | 3 |  | unimplemented | RW
41840 | V17 | 3 |  | unimplemented | RW
41841 | W17 | 3 |  | unimplemented | RW
41842 | V18 | 3 |  | unimplemented | RW
41843 | W18 | 3 |  | unimplemented | RW
41844 | V19 | 3 |  | unimplemented | RW
41845 | W19 | 3 |  | unimplemented | RW
41846 | V20 | 3 |  | unimplemented | RW
41847 | W20 | 3 |  | unimplemented | RW
41848 | CrvNam | 3 |  | unimplemented | RW
41856 | RmpPt1Tms | 3 |  | unimplemented | RW
41857 | RmpDecTmm | 3 |  | unimplemented | RW
41858 | RmpIncTmm | 3 |  | unimplemented | RW
41859 | ReadOnly | 3 |  | supported | R
41860 | ActPt | 4 |  | supported | RW
41861 | DeptRef | 4 |  | supported | RW
41862 | V1 | 4 |  | supported | RW
41863 | W1 | 4 |  | supported | RW
41864 | V2 | 4 |  | supported | RW
41865 | W2 | 4 |  | supported | RW
41866 | V3 | 4 |  | unimplemented | RW
41867 | W3 | 4 |  | unimplemented | RW
41868 | V4 | 4 |  | unimplemented | RW
41869 | W4 | 4 |  | unimplemented | RW
41870 | V5 | 4 |  | unimplemented | RW
41871 | W5 | 4 |  | unimplemented | RW
41872 | V6 | 4 |  | unimplemented | RW
41873 | W6 | 4 |  | unimplemented | RW
41874 | V7 | 4 |  | unimplemented | RW
41875 | W7 | 4 |  | unimplemented | RW
41876 | V8 | 4 |  | unimplemented | RW
41877 | W8 | 4 |  | unimplemented | RW
41878 | V9 | 4 |  | unimplemented | RW
41879 | W9 | 4 |  | unimplemented | RW
41880 | V10 | 4 |  | unimplemented | RW
41881 | W10 | 4 |  | unimplemented | RW
41882 | V11 | 4 |  | unimplemented | RW
41883 | W11 | 4 |  | unimplemented | RW
41884 | V12 | 4 |  | unimplemented | RW
41885 | W12 | 4 |  | unimplemented | RW
41886 | V13 | 4 |  | unimplemented | RW
41887 | W13 | 4 |  | unimplemented | RW
41888 | V14 | 4 |  | unimplemented | RW
41889 | W14 | 4 |  | unimplemented | RW
41890 | V15 | 4 |  | unimplemented | RW
41891 | W15 | 4 |  | unimplemented | RW
41892 | V16 | 4 |  | unimplemented | RW
41893 | W16 | 4 |  | unimplemented | RW
41894 | V17 | 4 |  | unimplemented | RW
41895 | W17 | 4 |  | unimplemented | RW
41896 | V18 | 4 |  | unimplemented | RW
41897 | W18 | 4 |  | unimplemented | RW
41898 | V19 | 4 |  | unimplemented | RW
41899 | W19 | 4 |  | unimplemented | RW
41900 | V20 | 4 |  | unimplemented | RW
41901 | W20 | 4 |  | unimplemented | RW
41902 | CrvNam | 4 |  | unimplemented | RW
41910 | RmpPt1Tms | 4 |  | unimplemented | RW
41911 | RmpDecTmm | 4 |  | unimplemented | RW
41912 | RmpIncTmm | 4 |  | unimplemented | RW
41913 | ReadOnly | 4 |  | supported | R

## 134
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
41914 | ID |  |  | 134
41915 | L |  |  | 242
41916 | ActCrv |  |  | supported | RW
41917 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
41918 | WinTms |  |  | unimplemented | RW
41919 | RvrtTms |  |  | unimplemented | RW
41920 | RmpTms |  |  | unimplemented | RW
41921 | NCrv |  |  | supported | R
41922 | NPt |  |  | supported | R
41923 | Hz_SF |  |  | -2 | R
41924 | W_SF |  |  | -1 | R
41925 | RmpIncDec_SF |  |  | 0 | R
41926 | ActPt | 1 |  | supported | RW
41927 | Hz1 | 1 |  | supported | RW
41928 | W1 | 1 |  | supported | RW
41929 | Hz2 | 1 |  | supported | RW
41930 | W2 | 1 |  | supported | RW
41931 | Hz3 | 1 |  | unimplemented | RW
41932 | W3 | 1 |  | unimplemented | RW
41933 | Hz4 | 1 |  | unimplemented | RW
41934 | W4 | 1 |  | unimplemented | RW
41935 | Hz5 | 1 |  | unimplemented | RW
41936 | W5 | 1 |  | unimplemented | RW
41937 | Hz6 | 1 |  | unimplemented | RW
41938 | W6 | 1 |  | unimplemented | RW
41939 | Hz7 | 1 |  | unimplemented | RW
41940 | W7 | 1 |  | unimplemented | RW
41941 | Hz8 | 1 |  | unimplemented | RW
41942 | W8 | 1 |  | unimplemented | RW
41943 | Hz9 | 1 |  | unimplemented | RW
41944 | W9 | 1 |  | unimplemented | RW
41945 | Hz10 | 1 |  | unimplemented | RW
41946 | W10 | 1 |  | unimplemented | RW
41947 | Hz11 | 1 |  | unimplemented | RW
41948 | W11 | 1 |  | unimplemented | RW
41949 | Hz12 | 1 |  | unimplemented | RW
41950 | W12 | 1 |  | unimplemented | RW
41951 | Hz13 | 1 |  | unimplemented | RW
41952 | W13 | 1 |  | unimplemented | RW
41953 | Hz14 | 1 |  | unimplemented | RW
41954 | W14 | 1 |  | unimplemented | RW
41955 | Hz15 | 1 |  | unimplemented | RW
41956 | W15 | 1 |  | unimplemented | RW
41957 | Hz16 | 1 |  | unimplemented | RW
41958 | W16 | 1 |  | unimplemented | RW
41959 | Hz17 | 1 |  | unimplemented | RW
41960 | W17 | 1 |  | unimplemented | RW
41961 | Hz18 | 1 |  | unimplemented | RW
41962 | W18 | 1 |  | unimplemented | RW
41963 | Hz19 | 1 |  | unimplemented | RW
41964 | W19 | 1 |  | unimplemented | RW
41965 | Hz20 | 1 |  | unimplemented | RW
41966 | W20 | 1 |  | unimplemented | RW
41967 | CrvNam | 1 |  | unimplemented | RW
41975 | RmpPT1Tms | 1 |  | unimplemented | RW
41976 | RmpDecTmm | 1 |  | unimplemented | RW
41977 | RmpIncTmm | 1 |  | unimplemented | RW
41978 | RmpRsUp | 1 |  | unimplemented | RW
41979 | SnptW | 1 |  | unimplemented | RW
41980 | WRef | 1 |  | unimplemented | RW
41981 | WRefStrHz | 1 |  | unimplemented | RW
41982 | WRefStopHz | 1 |  | unimplemented | RW
41983 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
41984 | ActPt | 2 |  | supported | RW
41985 | Hz1 | 2 |  | supported | RW
41986 | W1 | 2 |  | supported | RW
41987 | Hz2 | 2 |  | supported | RW
41988 | W2 | 2 |  | supported | RW
41989 | Hz3 | 2 |  | unimplemented | RW
41990 | W3 | 2 |  | unimplemented | RW
41991 | Hz4 | 2 |  | unimplemented | RW
41992 | W4 | 2 |  | unimplemented | RW
41993 | Hz5 | 2 |  | unimplemented | RW
41994 | W5 | 2 |  | unimplemented | RW
41995 | Hz6 | 2 |  | unimplemented | RW
41996 | W6 | 2 |  | unimplemented | RW
41997 | Hz7 | 2 |  | unimplemented | RW
41998 | W7 | 2 |  | unimplemented | RW
41999 | Hz8 | 2 |  | unimplemented | RW
42000 | W8 | 2 |  | unimplemented | RW
42001 | Hz9 | 2 |  | unimplemented | RW
42002 | W9 | 2 |  | unimplemented | RW
42003 | Hz10 | 2 |  | unimplemented | RW
42004 | W10 | 2 |  | unimplemented | RW
42005 | Hz11 | 2 |  | unimplemented | RW
42006 | W11 | 2 |  | unimplemented | RW
42007 | Hz12 | 2 |  | unimplemented | RW
42008 | W12 | 2 |  | unimplemented | RW
42009 | Hz13 | 2 |  | unimplemented | RW
42010 | W13 | 2 |  | unimplemented | RW
42011 | Hz14 | 2 |  | unimplemented | RW
42012 | W14 | 2 |  | unimplemented | RW
42013 | Hz15 | 2 |  | unimplemented | RW
42014 | W15 | 2 |  | unimplemented | RW
42015 | Hz16 | 2 |  | unimplemented | RW
42016 | W16 | 2 |  | unimplemented | RW
42017 | Hz17 | 2 |  | unimplemented | RW
42018 | W17 | 2 |  | unimplemented | RW
42019 | Hz18 | 2 |  | unimplemented | RW
42020 | W18 | 2 |  | unimplemented | RW
42021 | Hz19 | 2 |  | unimplemented | RW
42022 | W19 | 2 |  | unimplemented | RW
42023 | Hz20 | 2 |  | unimplemented | RW
42024 | W20 | 2 |  | unimplemented | RW
42025 | CrvNam | 2 |  | unimplemented | RW
42033 | RmpPT1Tms | 2 |  | unimplemented | RW
42034 | RmpDecTmm | 2 |  | unimplemented | RW
42035 | RmpIncTmm | 2 |  | unimplemented | RW
42036 | RmpRsUp | 2 |  | unimplemented | RW
42037 | SnptW | 2 |  | unimplemented | RW
42038 | WRef | 2 |  | unimplemented | RW
42039 | WRefStrHz | 2 |  | unimplemented | RW
42040 | WRefStopHz | 2 |  | unimplemented | RW
42041 | ReadOnly | 2 |  | supported | R
42042 | ActPt | 3 |  | supported | RW
42043 | Hz1 | 3 |  | supported | RW
42044 | W1 | 3 |  | supported | RW
42045 | Hz2 | 3 |  | supported | RW
42046 | W2 | 3 |  | supported | RW
42047 | Hz3 | 3 |  | unimplemented | RW
42048 | W3 | 3 |  | unimplemented | RW
42049 | Hz4 | 3 |  | unimplemented | RW
42050 | W4 | 3 |  | unimplemented | RW
42051 | Hz5 | 3 |  | unimplemented | RW
42052 | W5 | 3 |  | unimplemented | RW
42053 | Hz6 | 3 |  | unimplemented | RW
42054 | W6 | 3 |  | unimplemented | RW
42055 | Hz7 | 3 |  | unimplemented | RW
42056 | W7 | 3 |  | unimplemented | RW
42057 | Hz8 | 3 |  | unimplemented | RW
42058 | W8 | 3 |  | unimplemented | RW
42059 | Hz9 | 3 |  | unimplemented | RW
42060 | W9 | 3 |  | unimplemented | RW
42061 | Hz10 | 3 |  | unimplemented | RW
42062 | W10 | 3 |  | unimplemented | RW
42063 | Hz11 | 3 |  | unimplemented | RW
42064 | W11 | 3 |  | unimplemented | RW
42065 | Hz12 | 3 |  | unimplemented | RW
42066 | W12 | 3 |  | unimplemented | RW
42067 | Hz13 | 3 |  | unimplemented | RW
42068 | W13 | 3 |  | unimplemented | RW
42069 | Hz14 | 3 |  | unimplemented | RW
42070 | W14 | 3 |  | unimplemented | RW
42071 | Hz15 | 3 |  | unimplemented | RW
42072 | W15 | 3 |  | unimplemented | RW
42073 | Hz16 | 3 |  | unimplemented | RW
42074 | W16 | 3 |  | unimplemented | RW
42075 | Hz17 | 3 |  | unimplemented | RW
42076 | W17 | 3 |  | unimplemented | RW
42077 | Hz18 | 3 |  | unimplemented | RW
42078 | W18 | 3 |  | unimplemented | RW
42079 | Hz19 | 3 |  | unimplemented | RW
42080 | W19 | 3 |  | unimplemented | RW
42081 | Hz20 | 3 |  | unimplemented | RW
42082 | W20 | 3 |  | unimplemented | RW
42083 | CrvNam | 3 |  | unimplemented | RW
42091 | RmpPT1Tms | 3 |  | unimplemented | RW
42092 | RmpDecTmm | 3 |  | unimplemented | RW
42093 | RmpIncTmm | 3 |  | unimplemented | RW
42094 | RmpRsUp | 3 |  | unimplemented | RW
42095 | SnptW | 3 |  | unimplemented | RW
42096 | WRef | 3 |  | unimplemented | RW
42097 | WRefStrHz | 3 |  | unimplemented | RW
42098 | WRefStopHz | 3 |  | unimplemented | RW
42099 | ReadOnly | 3 |  | supported | R
42100 | ActPt | 4 |  | supported | RW
42101 | Hz1 | 4 |  | supported | RW
42102 | W1 | 4 |  | supported | RW
42103 | Hz2 | 4 |  | supported | RW
42104 | W2 | 4 |  | supported | RW
42105 | Hz3 | 4 |  | unimplemented | RW
42106 | W3 | 4 |  | unimplemented | RW
42107 | Hz4 | 4 |  | unimplemented | RW
42108 | W4 | 4 |  | unimplemented | RW
42109 | Hz5 | 4 |  | unimplemented | RW
42110 | W5 | 4 |  | unimplemented | RW
42111 | Hz6 | 4 |  | unimplemented | RW
42112 | W6 | 4 |  | unimplemented | RW
42113 | Hz7 | 4 |  | unimplemented | RW
42114 | W7 | 4 |  | unimplemented | RW
42115 | Hz8 | 4 |  | unimplemented | RW
42116 | W8 | 4 |  | unimplemented | RW
42117 | Hz9 | 4 |  | unimplemented | RW
42118 | W9 | 4 |  | unimplemented | RW
42119 | Hz10 | 4 |  | unimplemented | RW
42120 | W10 | 4 |  | unimplemented | RW
42121 | Hz11 | 4 |  | unimplemented | RW
42122 | W11 | 4 |  | unimplemented | RW
42123 | Hz12 | 4 |  | unimplemented | RW
42124 | W12 | 4 |  | unimplemented | RW
42125 | Hz13 | 4 |  | unimplemented | RW
42126 | W13 | 4 |  | unimplemented | RW
42127 | Hz14 | 4 |  | unimplemented | RW
42128 | W14 | 4 |  | unimplemented | RW
42129 | Hz15 | 4 |  | unimplemented | RW
42130 | W15 | 4 |  | unimplemented | RW
42131 | Hz16 | 4 |  | unimplemented | RW
42132 | W16 | 4 |  | unimplemented | RW
42133 | Hz17 | 4 |  | unimplemented | RW
42134 | W17 | 4 |  | unimplemented | RW
42135 | Hz18 | 4 |  | unimplemented | RW
42136 | W18 | 4 |  | unimplemented | RW
42137 | Hz19 | 4 |  | unimplemented | RW
42138 | W19 | 4 |  | unimplemented | RW
42139 | Hz20 | 4 |  | unimplemented | RW
42140 | W20 | 4 |  | unimplemented | RW
42141 | CrvNam | 4 |  | unimplemented | RW
42149 | RmpPT1Tms | 4 |  | unimplemented | RW
42150 | RmpDecTmm | 4 |  | unimplemented | RW
42151 | RmpIncTmm | 4 |  | unimplemented | RW
42152 | RmpRsUp | 4 |  | unimplemented | RW
42153 | SnptW | 4 |  | unimplemented | RW
42154 | WRef | 4 |  | unimplemented | RW
42155 | WRefStrHz | 4 |  | unimplemented | RW
42156 | WRefStopHz | 4 |  | unimplemented | RW
42157 | ReadOnly | 4 |  | supported | R

## 135
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
42158 | ID |  |  | 135
42159 | L |  |  | 210
42160 | ActCrv |  |  | supported | RW
42161 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
42162 | WinTms |  |  | unimplemented | RW
42163 | RvrtTms |  |  | unimplemented | RW
42164 | RmpTms |  |  | unimplemented | RW
42165 | NCrv |  |  | supported | R
42166 | NPt |  |  | supported | R
42167 | Tms_SF |  |  | -2 | R
42168 | Hz_SF |  |  | -2 | R
42169 | Pad |  |  |  | R
42170 | ActPt | 1 |  | supported | RW
42171 | Tms1 | 1 |  | supported | RW
42172 | Hz1 | 1 |  | supported | RW
42173 | Tms2 | 1 |  | supported | RW
42174 | Hz2 | 1 |  | supported | RW
42175 | Tms3 | 1 |  | supported | RW
42176 | Hz3 | 1 |  | supported | RW
42177 | Tms4 | 1 |  | supported | RW
42178 | Hz4 | 1 |  | supported | RW
42179 | Tms5 | 1 |  | supported | RW
42180 | Hz5 | 1 |  | supported | RW
42181 | Tms6 | 1 |  | supported | RW
42182 | Hz6 | 1 |  | supported | RW
42183 | Tms7 | 1 |  | supported | RW
42184 | Hz7 | 1 |  | supported | RW
42185 | Tms8 | 1 |  | supported | RW
42186 | Hz8 | 1 |  | supported | RW
42187 | Tms9 | 1 |  | supported | RW
42188 | Hz9 | 1 |  | supported | RW
42189 | Tms10 | 1 |  | supported | RW
42190 | Hz10 | 1 |  | supported | RW
42191 | Tms11 | 1 |  | unimplemented | RW
42192 | Hz11 | 1 |  | unimplemented | RW
42193 | Tms12 | 1 |  | unimplemented | RW
42194 | Hz12 | 1 |  | unimplemented | RW
42195 | Tms13 | 1 |  | unimplemented | RW
42196 | Hz13 | 1 |  | unimplemented | RW
42197 | Tms14 | 1 |  | unimplemented | RW
42198 | Hz14 | 1 |  | unimplemented | RW
42199 | Tms15 | 1 |  | unimplemented | RW
42200 | Hz15 | 1 |  | unimplemented | RW
42201 | Tms16 | 1 |  | unimplemented | RW
42202 | Hz16 | 1 |  | unimplemented | RW
42203 | Tms17 | 1 |  | unimplemented | RW
42204 | Hz17 | 1 |  | unimplemented | RW
42205 | Tms18 | 1 |  | unimplemented | RW
42206 | Hz18 | 1 |  | unimplemented | RW
42207 | Tms19 | 1 |  | unimplemented | RW
42208 | Hz19 | 1 |  | unimplemented | RW
42209 | Tms20 | 1 |  | unimplemented | RW
42210 | Hz20 | 1 |  | unimplemented | RW
42211 | CrvNam | 1 |  | unimplemented | RW
42219 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
42220 | ActPt | 2 |  | supported | RW
42221 | Tms1 | 2 |  | supported | RW
42222 | Hz1 | 2 |  | supported | RW
42223 | Tms2 | 2 |  | supported | RW
42224 | Hz2 | 2 |  | supported | RW
42225 | Tms3 | 2 |  | supported | RW
42226 | Hz3 | 2 |  | supported | RW
42227 | Tms4 | 2 |  | supported | RW
42228 | Hz4 | 2 |  | supported | RW
42229 | Tms5 | 2 |  | supported | RW
42230 | Hz5 | 2 |  | supported | RW
42231 | Tms6 | 2 |  | supported | RW
42232 | Hz6 | 2 |  | supported | RW
42233 | Tms7 | 2 |  | supported | RW
42234 | Hz7 | 2 |  | supported | RW
42235 | Tms8 | 2 |  | supported | RW
42236 | Hz8 | 2 |  | supported | RW
42237 | Tms9 | 2 |  | supported | RW
42238 | Hz9 | 2 |  | supported | RW
42239 | Tms10 | 2 |  | supported | RW
42240 | Hz10 | 2 |  | supported | RW
42241 | Tms11 | 2 |  | unimplemented | RW
42242 | Hz11 | 2 |  | unimplemented | RW
42243 | Tms12 | 2 |  | unimplemented | RW
42244 | Hz12 | 2 |  | unimplemented | RW
42245 | Tms13 | 2 |  | unimplemented | RW
42246 | Hz13 | 2 |  | unimplemented | RW
42247 | Tms14 | 2 |  | unimplemented | RW
42248 | Hz14 | 2 |  | unimplemented | RW
42249 | Tms15 | 2 |  | unimplemented | RW
42250 | Hz15 | 2 |  | unimplemented | RW
42251 | Tms16 | 2 |  | unimplemented | RW
42252 | Hz16 | 2 |  | unimplemented | RW
42253 | Tms17 | 2 |  | unimplemented | RW
42254 | Hz17 | 2 |  | unimplemented | RW
42255 | Tms18 | 2 |  | unimplemented | RW
42256 | Hz18 | 2 |  | unimplemented | RW
42257 | Tms19 | 2 |  | unimplemented | RW
42258 | Hz19 | 2 |  | unimplemented | RW
42259 | Tms20 | 2 |  | unimplemented | RW
42260 | Hz20 | 2 |  | unimplemented | RW
42261 | CrvNam | 2 |  | unimplemented | RW
42269 | ReadOnly | 2 |  | supported | R
42270 | ActPt | 3 |  | supported | RW
42271 | Tms1 | 3 |  | supported | RW
42272 | Hz1 | 3 |  | supported | RW
42273 | Tms2 | 3 |  | supported | RW
42274 | Hz2 | 3 |  | supported | RW
42275 | Tms3 | 3 |  | supported | RW
42276 | Hz3 | 3 |  | supported | RW
42277 | Tms4 | 3 |  | supported | RW
42278 | Hz4 | 3 |  | supported | RW
42279 | Tms5 | 3 |  | supported | RW
42280 | Hz5 | 3 |  | supported | RW
42281 | Tms6 | 3 |  | supported | RW
42282 | Hz6 | 3 |  | supported | RW
42283 | Tms7 | 3 |  | supported | RW
42284 | Hz7 | 3 |  | supported | RW
42285 | Tms8 | 3 |  | supported | RW
42286 | Hz8 | 3 |  | supported | RW
42287 | Tms9 | 3 |  | supported | RW
42288 | Hz9 | 3 |  | supported | RW
42289 | Tms10 | 3 |  | supported | RW
42290 | Hz10 | 3 |  | supported | RW
42291 | Tms11 | 3 |  | unimplemented | RW
42292 | Hz11 | 3 |  | unimplemented | RW
42293 | Tms12 | 3 |  | unimplemented | RW
42294 | Hz12 | 3 |  | unimplemented | RW
42295 | Tms13 | 3 |  | unimplemented | RW
42296 | Hz13 | 3 |  | unimplemented | RW
42297 | Tms14 | 3 |  | unimplemented | RW
42298 | Hz14 | 3 |  | unimplemented | RW
42299 | Tms15 | 3 |  | unimplemented | RW
42300 | Hz15 | 3 |  | unimplemented | RW
42301 | Tms16 | 3 |  | unimplemented | RW
42302 | Hz16 | 3 |  | unimplemented | RW
42303 | Tms17 | 3 |  | unimplemented | RW
42304 | Hz17 | 3 |  | unimplemented | RW
42305 | Tms18 | 3 |  | unimplemented | RW
42306 | Hz18 | 3 |  | unimplemented | RW
42307 | Tms19 | 3 |  | unimplemented | RW
42308 | Hz19 | 3 |  | unimplemented | RW
42309 | Tms20 | 3 |  | unimplemented | RW
42310 | Hz20 | 3 |  | unimplemented | RW
42311 | CrvNam | 3 |  | unimplemented | RW
42319 | ReadOnly | 3 |  | supported | R
42320 | ActPt | 4 |  | supported | RW
42321 | Tms1 | 4 |  | supported | RW
42322 | Hz1 | 4 |  | supported | RW
42323 | Tms2 | 4 |  | supported | RW
42324 | Hz2 | 4 |  | supported | RW
42325 | Tms3 | 4 |  | supported | RW
42326 | Hz3 | 4 |  | supported | RW
42327 | Tms4 | 4 |  | supported | RW
42328 | Hz4 | 4 |  | supported | RW
42329 | Tms5 | 4 |  | supported | RW
42330 | Hz5 | 4 |  | supported | RW
42331 | Tms6 | 4 |  | supported | RW
42332 | Hz6 | 4 |  | supported | RW
42333 | Tms7 | 4 |  | supported | RW
42334 | Hz7 | 4 |  | supported | RW
42335 | Tms8 | 4 |  | supported | RW
42336 | Hz8 | 4 |  | supported | RW
42337 | Tms9 | 4 |  | supported | RW
42338 | Hz9 | 4 |  | supported | RW
42339 | Tms10 | 4 |  | supported | RW
42340 | Hz10 | 4 |  | supported | RW
42341 | Tms11 | 4 |  | unimplemented | RW
42342 | Hz11 | 4 |  | unimplemented | RW
42343 | Tms12 | 4 |  | unimplemented | RW
42344 | Hz12 | 4 |  | unimplemented | RW
42345 | Tms13 | 4 |  | unimplemented | RW
42346 | Hz13 | 4 |  | unimplemented | RW
42347 | Tms14 | 4 |  | unimplemented | RW
42348 | Hz14 | 4 |  | unimplemented | RW
42349 | Tms15 | 4 |  | unimplemented | RW
42350 | Hz15 | 4 |  | unimplemented | RW
42351 | Tms16 | 4 |  | unimplemented | RW
42352 | Hz16 | 4 |  | unimplemented | RW
42353 | Tms17 | 4 |  | unimplemented | RW
42354 | Hz17 | 4 |  | unimplemented | RW
42355 | Tms18 | 4 |  | unimplemented | RW
42356 | Hz18 | 4 |  | unimplemented | RW
42357 | Tms19 | 4 |  | unimplemented | RW
42358 | Hz19 | 4 |  | unimplemented | RW
42359 | Tms20 | 4 |  | unimplemented | RW
42360 | Hz20 | 4 |  | unimplemented | RW
42361 | CrvNam | 4 |  | unimplemented | RW
42369 | ReadOnly | 4 |  | supported | R

## 64256
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
42370 | ID |  |  | 64256
42371 | L |  |  | 370
42372 | ActCrv |  |  | supported | RW
42373 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
42374 | WinTms |  |  | unimplemented | RW
42375 | RvrtTms |  |  | unimplemented | RW
42376 | RmpTms |  |  | unimplemented | RW
42377 | NCrv |  |  | supported | R
42378 | NPt |  |  | supported | R
42379 | Tms_SF |  |  | -6 | R
42380 | Hz_SF |  |  | -2 | R
42381 | Pad |  |  |  | R
42382 | ActPt | 1 |  | supported | RW
42383 | Tms1 | 1 |  | supported | RW
42385 | Hz1 | 1 |  | supported | RW
42386 | Fn1 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42387 | Tms2 | 1 |  | supported | RW
42389 | Hz2 | 1 |  | supported | RW
42390 | Fn2 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42391 | Tms3 | 1 |  | supported | RW
42393 | Hz3 | 1 |  | supported | RW
42394 | Fn3 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42395 | Tms4 | 1 |  | supported | RW
42397 | Hz4 | 1 |  | supported | RW
42398 | Fn4 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42399 | Tms5 | 1 |  | supported | RW
42401 | Hz5 | 1 |  | supported | RW
42402 | Fn5 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42403 | Tms6 | 1 |  | supported | RW
42405 | Hz6 | 1 |  | supported | RW
42406 | Fn6 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42407 | Tms7 | 1 |  | supported | RW
42409 | Hz7 | 1 |  | supported | RW
42410 | Fn7 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42411 | Tms8 | 1 |  | supported | RW
42413 | Hz8 | 1 |  | supported | RW
42414 | Fn8 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42415 | Tms9 | 1 |  | supported | RW
42417 | Hz9 | 1 |  | supported | RW
42418 | Fn9 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42419 | Tms10 | 1 |  | supported | RW
42421 | Hz10 | 1 |  | supported | RW
42422 | Fn10 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42423 | Tms11 | 1 |  | unimplemented | RW
42425 | Hz11 | 1 |  | unimplemented | RW
42426 | Fn11 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42427 | Tms12 | 1 |  | unimplemented | RW
42429 | Hz12 | 1 |  | unimplemented | RW
42430 | Fn12 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42431 | Tms13 | 1 |  | unimplemented | RW
42433 | Hz13 | 1 |  | unimplemented | RW
42434 | Fn13 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42435 | Tms14 | 1 |  | unimplemented | RW
42437 | Hz14 | 1 |  | unimplemented | RW
42438 | Fn14 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42439 | Tms15 | 1 |  | unimplemented | RW
42441 | Hz15 | 1 |  | unimplemented | RW
42442 | Fn15 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42443 | Tms16 | 1 |  | unimplemented | RW
42445 | Hz16 | 1 |  | unimplemented | RW
42446 | Fn16 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42447 | Tms17 | 1 |  | unimplemented | RW
42449 | Hz17 | 1 |  | unimplemented | RW
42450 | Fn17 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42451 | Tms18 | 1 |  | unimplemented | RW
42453 | Hz18 | 1 |  | unimplemented | RW
42454 | Fn18 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42455 | Tms19 | 1 |  | unimplemented | RW
42457 | Hz19 | 1 |  | unimplemented | RW
42458 | Fn19 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42459 | Tms20 | 1 |  | unimplemented | RW
42461 | Hz20 | 1 |  | unimplemented | RW
42462 | Fn20 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
42463 | CrvNam | 1 |  | unimplemented | RW
42471 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
42472 | ActPt | 2 |  | supported | RW
42473 | Tms1 | 2 |  | supported | RW
42475 | Hz1 | 2 |  | supported | RW
42476 | Fn1 | 2 |  | supported | RW
42477 | Tms2 | 2 |  | supported | RW
42479 | Hz2 | 2 |  | supported | RW
42480 | Fn2 | 2 |  | supported | RW
42481 | Tms3 | 2 |  | supported | RW
42483 | Hz3 | 2 |  | supported | RW
42484 | Fn3 | 2 |  | supported | RW
42485 | Tms4 | 2 |  | supported | RW
42487 | Hz4 | 2 |  | supported | RW
42488 | Fn4 | 2 |  | supported | RW
42489 | Tms5 | 2 |  | supported | RW
42491 | Hz5 | 2 |  | supported | RW
42492 | Fn5 | 2 |  | supported | RW
42493 | Tms6 | 2 |  | supported | RW
42495 | Hz6 | 2 |  | supported | RW
42496 | Fn6 | 2 |  | supported | RW
42497 | Tms7 | 2 |  | supported | RW
42499 | Hz7 | 2 |  | supported | RW
42500 | Fn7 | 2 |  | supported | RW
42501 | Tms8 | 2 |  | supported | RW
42503 | Hz8 | 2 |  | supported | RW
42504 | Fn8 | 2 |  | supported | RW
42505 | Tms9 | 2 |  | supported | RW
42507 | Hz9 | 2 |  | supported | RW
42508 | Fn9 | 2 |  | supported | RW
42509 | Tms10 | 2 |  | supported | RW
42511 | Hz10 | 2 |  | supported | RW
42512 | Fn10 | 2 |  | supported | RW
42513 | Tms11 | 2 |  | unimplemented | RW
42515 | Hz11 | 2 |  | unimplemented | RW
42516 | Fn11 | 2 |  | unimplemented | RW
42517 | Tms12 | 2 |  | unimplemented | RW
42519 | Hz12 | 2 |  | unimplemented | RW
42520 | Fn12 | 2 |  | unimplemented | RW
42521 | Tms13 | 2 |  | unimplemented | RW
42523 | Hz13 | 2 |  | unimplemented | RW
42524 | Fn13 | 2 |  | unimplemented | RW
42525 | Tms14 | 2 |  | unimplemented | RW
42527 | Hz14 | 2 |  | unimplemented | RW
42528 | Fn14 | 2 |  | unimplemented | RW
42529 | Tms15 | 2 |  | unimplemented | RW
42531 | Hz15 | 2 |  | unimplemented | RW
42532 | Fn15 | 2 |  | unimplemented | RW
42533 | Tms16 | 2 |  | unimplemented | RW
42535 | Hz16 | 2 |  | unimplemented | RW
42536 | Fn16 | 2 |  | unimplemented | RW
42537 | Tms17 | 2 |  | unimplemented | RW
42539 | Hz17 | 2 |  | unimplemented | RW
42540 | Fn17 | 2 |  | unimplemented | RW
42541 | Tms18 | 2 |  | unimplemented | RW
42543 | Hz18 | 2 |  | unimplemented | RW
42544 | Fn18 | 2 |  | unimplemented | RW
42545 | Tms19 | 2 |  | unimplemented | RW
42547 | Hz19 | 2 |  | unimplemented | RW
42548 | Fn19 | 2 |  | unimplemented | RW
42549 | Tms20 | 2 |  | unimplemented | RW
42551 | Hz20 | 2 |  | unimplemented | RW
42552 | Fn20 | 2 |  | unimplemented | RW
42553 | CrvNam | 2 |  | unimplemented | RW
42561 | ReadOnly | 2 |  | supported | R
42562 | ActPt | 3 |  | supported | RW
42563 | Tms1 | 3 |  | supported | RW
42565 | Hz1 | 3 |  | supported | RW
42566 | Fn1 | 3 |  | supported | RW
42567 | Tms2 | 3 |  | supported | RW
42569 | Hz2 | 3 |  | supported | RW
42570 | Fn2 | 3 |  | supported | RW
42571 | Tms3 | 3 |  | supported | RW
42573 | Hz3 | 3 |  | supported | RW
42574 | Fn3 | 3 |  | supported | RW
42575 | Tms4 | 3 |  | supported | RW
42577 | Hz4 | 3 |  | supported | RW
42578 | Fn4 | 3 |  | supported | RW
42579 | Tms5 | 3 |  | supported | RW
42581 | Hz5 | 3 |  | supported | RW
42582 | Fn5 | 3 |  | supported | RW
42583 | Tms6 | 3 |  | supported | RW
42585 | Hz6 | 3 |  | supported | RW
42586 | Fn6 | 3 |  | supported | RW
42587 | Tms7 | 3 |  | supported | RW
42589 | Hz7 | 3 |  | supported | RW
42590 | Fn7 | 3 |  | supported | RW
42591 | Tms8 | 3 |  | supported | RW
42593 | Hz8 | 3 |  | supported | RW
42594 | Fn8 | 3 |  | supported | RW
42595 | Tms9 | 3 |  | supported | RW
42597 | Hz9 | 3 |  | supported | RW
42598 | Fn9 | 3 |  | supported | RW
42599 | Tms10 | 3 |  | supported | RW
42601 | Hz10 | 3 |  | supported | RW
42602 | Fn10 | 3 |  | supported | RW
42603 | Tms11 | 3 |  | unimplemented | RW
42605 | Hz11 | 3 |  | unimplemented | RW
42606 | Fn11 | 3 |  | unimplemented | RW
42607 | Tms12 | 3 |  | unimplemented | RW
42609 | Hz12 | 3 |  | unimplemented | RW
42610 | Fn12 | 3 |  | unimplemented | RW
42611 | Tms13 | 3 |  | unimplemented | RW
42613 | Hz13 | 3 |  | unimplemented | RW
42614 | Fn13 | 3 |  | unimplemented | RW
42615 | Tms14 | 3 |  | unimplemented | RW
42617 | Hz14 | 3 |  | unimplemented | RW
42618 | Fn14 | 3 |  | unimplemented | RW
42619 | Tms15 | 3 |  | unimplemented | RW
42621 | Hz15 | 3 |  | unimplemented | RW
42622 | Fn15 | 3 |  | unimplemented | RW
42623 | Tms16 | 3 |  | unimplemented | RW
42625 | Hz16 | 3 |  | unimplemented | RW
42626 | Fn16 | 3 |  | unimplemented | RW
42627 | Tms17 | 3 |  | unimplemented | RW
42629 | Hz17 | 3 |  | unimplemented | RW
42630 | Fn17 | 3 |  | unimplemented | RW
42631 | Tms18 | 3 |  | unimplemented | RW
42633 | Hz18 | 3 |  | unimplemented | RW
42634 | Fn18 | 3 |  | unimplemented | RW
42635 | Tms19 | 3 |  | unimplemented | RW
42637 | Hz19 | 3 |  | unimplemented | RW
42638 | Fn19 | 3 |  | unimplemented | RW
42639 | Tms20 | 3 |  | unimplemented | RW
42641 | Hz20 | 3 |  | unimplemented | RW
42642 | Fn20 | 3 |  | unimplemented | RW
42643 | CrvNam | 3 |  | unimplemented | RW
42651 | ReadOnly | 3 |  | supported | R
42652 | ActPt | 4 |  | supported | RW
42653 | Tms1 | 4 |  | supported | RW
42655 | Hz1 | 4 |  | supported | RW
42656 | Fn1 | 4 |  | supported | RW
42657 | Tms2 | 4 |  | supported | RW
42659 | Hz2 | 4 |  | supported | RW
42660 | Fn2 | 4 |  | supported | RW
42661 | Tms3 | 4 |  | supported | RW
42663 | Hz3 | 4 |  | supported | RW
42664 | Fn3 | 4 |  | supported | RW
42665 | Tms4 | 4 |  | supported | RW
42667 | Hz4 | 4 |  | supported | RW
42668 | Fn4 | 4 |  | supported | RW
42669 | Tms5 | 4 |  | supported | RW
42671 | Hz5 | 4 |  | supported | RW
42672 | Fn5 | 4 |  | supported | RW
42673 | Tms6 | 4 |  | supported | RW
42675 | Hz6 | 4 |  | supported | RW
42676 | Fn6 | 4 |  | supported | RW
42677 | Tms7 | 4 |  | supported | RW
42679 | Hz7 | 4 |  | supported | RW
42680 | Fn7 | 4 |  | supported | RW
42681 | Tms8 | 4 |  | supported | RW
42683 | Hz8 | 4 |  | supported | RW
42684 | Fn8 | 4 |  | supported | RW
42685 | Tms9 | 4 |  | supported | RW
42687 | Hz9 | 4 |  | supported | RW
42688 | Fn9 | 4 |  | supported | RW
42689 | Tms10 | 4 |  | supported | RW
42691 | Hz10 | 4 |  | supported | RW
42692 | Fn10 | 4 |  | supported | RW
42693 | Tms11 | 4 |  | unimplemented | RW
42695 | Hz11 | 4 |  | unimplemented | RW
42696 | Fn11 | 4 |  | unimplemented | RW
42697 | Tms12 | 4 |  | unimplemented | RW
42699 | Hz12 | 4 |  | unimplemented | RW
42700 | Fn12 | 4 |  | unimplemented | RW
42701 | Tms13 | 4 |  | unimplemented | RW
42703 | Hz13 | 4 |  | unimplemented | RW
42704 | Fn13 | 4 |  | unimplemented | RW
42705 | Tms14 | 4 |  | unimplemented | RW
42707 | Hz14 | 4 |  | unimplemented | RW
42708 | Fn14 | 4 |  | unimplemented | RW
42709 | Tms15 | 4 |  | unimplemented | RW
42711 | Hz15 | 4 |  | unimplemented | RW
42712 | Fn15 | 4 |  | unimplemented | RW
42713 | Tms16 | 4 |  | unimplemented | RW
42715 | Hz16 | 4 |  | unimplemented | RW
42716 | Fn16 | 4 |  | unimplemented | RW
42717 | Tms17 | 4 |  | unimplemented | RW
42719 | Hz17 | 4 |  | unimplemented | RW
42720 | Fn17 | 4 |  | unimplemented | RW
42721 | Tms18 | 4 |  | unimplemented | RW
42723 | Hz18 | 4 |  | unimplemented | RW
42724 | Fn18 | 4 |  | unimplemented | RW
42725 | Tms19 | 4 |  | unimplemented | RW
42727 | Hz19 | 4 |  | unimplemented | RW
42728 | Fn19 | 4 |  | unimplemented | RW
42729 | Tms20 | 4 |  | unimplemented | RW
42731 | Hz20 | 4 |  | unimplemented | RW
42732 | Fn20 | 4 |  | unimplemented | RW
42733 | CrvNam | 4 |  | unimplemented | RW
42741 | ReadOnly | 4 |  | supported | R

## 136
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
42742 | ID |  |  | 136
42743 | L |  |  | 210
42744 | ActCrv |  |  | supported | RW
42745 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
42746 | WinTms |  |  | unimplemented | RW
42747 | RvrtTms |  |  | unimplemented | RW
42748 | RmpTms |  |  | unimplemented | RW
42749 | NCrv |  |  | supported | R
42750 | NPt |  |  | supported | R
42751 | Tms_SF |  |  | -2 | R
42752 | Hz_SF |  |  | -2 | R
42753 | Pad |  |  |  | R
42754 | ActPt | 1 |  | supported | RW
42755 | Tms1 | 1 |  | supported | RW
42756 | Hz1 | 1 |  | supported | RW
42757 | Tms2 | 1 |  | supported | RW
42758 | Hz2 | 1 |  | supported | RW
42759 | Tms3 | 1 |  | supported | RW
42760 | Hz3 | 1 |  | supported | RW
42761 | Tms4 | 1 |  | supported | RW
42762 | Hz4 | 1 |  | supported | RW
42763 | Tms5 | 1 |  | supported | RW
42764 | Hz5 | 1 |  | supported | RW
42765 | Tms6 | 1 |  | supported | RW
42766 | Hz6 | 1 |  | supported | RW
42767 | Tms7 | 1 |  | supported | RW
42768 | Hz7 | 1 |  | supported | RW
42769 | Tms8 | 1 |  | supported | RW
42770 | Hz8 | 1 |  | supported | RW
42771 | Tms9 | 1 |  | supported | RW
42772 | Hz9 | 1 |  | supported | RW
42773 | Tms10 | 1 |  | supported | RW
42774 | Hz10 | 1 |  | supported | RW
42775 | Tms11 | 1 |  | unimplemented | RW
42776 | Hz11 | 1 |  | unimplemented | RW
42777 | Tms12 | 1 |  | unimplemented | RW
42778 | Hz12 | 1 |  | unimplemented | RW
42779 | Tms13 | 1 |  | unimplemented | RW
42780 | Hz13 | 1 |  | unimplemented | RW
42781 | Tms14 | 1 |  | unimplemented | RW
42782 | Hz14 | 1 |  | unimplemented | RW
42783 | Tms15 | 1 |  | unimplemented | RW
42784 | Hz15 | 1 |  | unimplemented | RW
42785 | Tms16 | 1 |  | unimplemented | RW
42786 | Hz16 | 1 |  | unimplemented | RW
42787 | Tms17 | 1 |  | unimplemented | RW
42788 | Hz17 | 1 |  | unimplemented | RW
42789 | Tms18 | 1 |  | unimplemented | RW
42790 | Hz18 | 1 |  | unimplemented | RW
42791 | Tms19 | 1 |  | unimplemented | RW
42792 | Hz19 | 1 |  | unimplemented | RW
42793 | Tms20 | 1 |  | unimplemented | RW
42794 | Hz20 | 1 |  | unimplemented | RW
42795 | CrvNam | 1 |  | unimplemented | RW
42803 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
42804 | ActPt | 2 |  | supported | RW
42805 | Tms1 | 2 |  | supported | RW
42806 | Hz1 | 2 |  | supported | RW
42807 | Tms2 | 2 |  | supported | RW
42808 | Hz2 | 2 |  | supported | RW
42809 | Tms3 | 2 |  | supported | RW
42810 | Hz3 | 2 |  | supported | RW
42811 | Tms4 | 2 |  | supported | RW
42812 | Hz4 | 2 |  | supported | RW
42813 | Tms5 | 2 |  | supported | RW
42814 | Hz5 | 2 |  | supported | RW
42815 | Tms6 | 2 |  | supported | RW
42816 | Hz6 | 2 |  | supported | RW
42817 | Tms7 | 2 |  | supported | RW
42818 | Hz7 | 2 |  | supported | RW
42819 | Tms8 | 2 |  | supported | RW
42820 | Hz8 | 2 |  | supported | RW
42821 | Tms9 | 2 |  | supported | RW
42822 | Hz9 | 2 |  | supported | RW
42823 | Tms10 | 2 |  | supported | RW
42824 | Hz10 | 2 |  | supported | RW
42825 | Tms11 | 2 |  | unimplemented | RW
42826 | Hz11 | 2 |  | unimplemented | RW
42827 | Tms12 | 2 |  | unimplemented | RW
42828 | Hz12 | 2 |  | unimplemented | RW
42829 | Tms13 | 2 |  | unimplemented | RW
42830 | Hz13 | 2 |  | unimplemented | RW
42831 | Tms14 | 2 |  | unimplemented | RW
42832 | Hz14 | 2 |  | unimplemented | RW
42833 | Tms15 | 2 |  | unimplemented | RW
42834 | Hz15 | 2 |  | unimplemented | RW
42835 | Tms16 | 2 |  | unimplemented | RW
42836 | Hz16 | 2 |  | unimplemented | RW
42837 | Tms17 | 2 |  | unimplemented | RW
42838 | Hz17 | 2 |  | unimplemented | RW
42839 | Tms18 | 2 |  | unimplemented | RW
42840 | Hz18 | 2 |  | unimplemented | RW
42841 | Tms19 | 2 |  | unimplemented | RW
42842 | Hz19 | 2 |  | unimplemented | RW
42843 | Tms20 | 2 |  | unimplemented | RW
42844 | Hz20 | 2 |  | unimplemented | RW
42845 | CrvNam | 2 |  | unimplemented | RW
42853 | ReadOnly | 2 |  | supported | R
42854 | ActPt | 3 |  | supported | RW
42855 | Tms1 | 3 |  | supported | RW
42856 | Hz1 | 3 |  | supported | RW
42857 | Tms2 | 3 |  | supported | RW
42858 | Hz2 | 3 |  | supported | RW
42859 | Tms3 | 3 |  | supported | RW
42860 | Hz3 | 3 |  | supported | RW
42861 | Tms4 | 3 |  | supported | RW
42862 | Hz4 | 3 |  | supported | RW
42863 | Tms5 | 3 |  | supported | RW
42864 | Hz5 | 3 |  | supported | RW
42865 | Tms6 | 3 |  | supported | RW
42866 | Hz6 | 3 |  | supported | RW
42867 | Tms7 | 3 |  | supported | RW
42868 | Hz7 | 3 |  | supported | RW
42869 | Tms8 | 3 |  | supported | RW
42870 | Hz8 | 3 |  | supported | RW
42871 | Tms9 | 3 |  | supported | RW
42872 | Hz9 | 3 |  | supported | RW
42873 | Tms10 | 3 |  | supported | RW
42874 | Hz10 | 3 |  | supported | RW
42875 | Tms11 | 3 |  | unimplemented | RW
42876 | Hz11 | 3 |  | unimplemented | RW
42877 | Tms12 | 3 |  | unimplemented | RW
42878 | Hz12 | 3 |  | unimplemented | RW
42879 | Tms13 | 3 |  | unimplemented | RW
42880 | Hz13 | 3 |  | unimplemented | RW
42881 | Tms14 | 3 |  | unimplemented | RW
42882 | Hz14 | 3 |  | unimplemented | RW
42883 | Tms15 | 3 |  | unimplemented | RW
42884 | Hz15 | 3 |  | unimplemented | RW
42885 | Tms16 | 3 |  | unimplemented | RW
42886 | Hz16 | 3 |  | unimplemented | RW
42887 | Tms17 | 3 |  | unimplemented | RW
42888 | Hz17 | 3 |  | unimplemented | RW
42889 | Tms18 | 3 |  | unimplemented | RW
42890 | Hz18 | 3 |  | unimplemented | RW
42891 | Tms19 | 3 |  | unimplemented | RW
42892 | Hz19 | 3 |  | unimplemented | RW
42893 | Tms20 | 3 |  | unimplemented | RW
42894 | Hz20 | 3 |  | unimplemented | RW
42895 | CrvNam | 3 |  | unimplemented | RW
42903 | ReadOnly | 3 |  | supported | R
42904 | ActPt | 4 |  | supported | RW
42905 | Tms1 | 4 |  | supported | RW
42906 | Hz1 | 4 |  | supported | RW
42907 | Tms2 | 4 |  | supported | RW
42908 | Hz2 | 4 |  | supported | RW
42909 | Tms3 | 4 |  | supported | RW
42910 | Hz3 | 4 |  | supported | RW
42911 | Tms4 | 4 |  | supported | RW
42912 | Hz4 | 4 |  | supported | RW
42913 | Tms5 | 4 |  | supported | RW
42914 | Hz5 | 4 |  | supported | RW
42915 | Tms6 | 4 |  | supported | RW
42916 | Hz6 | 4 |  | supported | RW
42917 | Tms7 | 4 |  | supported | RW
42918 | Hz7 | 4 |  | supported | RW
42919 | Tms8 | 4 |  | supported | RW
42920 | Hz8 | 4 |  | supported | RW
42921 | Tms9 | 4 |  | supported | RW
42922 | Hz9 | 4 |  | supported | RW
42923 | Tms10 | 4 |  | supported | RW
42924 | Hz10 | 4 |  | supported | RW
42925 | Tms11 | 4 |  | unimplemented | RW
42926 | Hz11 | 4 |  | unimplemented | RW
42927 | Tms12 | 4 |  | unimplemented | RW
42928 | Hz12 | 4 |  | unimplemented | RW
42929 | Tms13 | 4 |  | unimplemented | RW
42930 | Hz13 | 4 |  | unimplemented | RW
42931 | Tms14 | 4 |  | unimplemented | RW
42932 | Hz14 | 4 |  | unimplemented | RW
42933 | Tms15 | 4 |  | unimplemented | RW
42934 | Hz15 | 4 |  | unimplemented | RW
42935 | Tms16 | 4 |  | unimplemented | RW
42936 | Hz16 | 4 |  | unimplemented | RW
42937 | Tms17 | 4 |  | unimplemented | RW
42938 | Hz17 | 4 |  | unimplemented | RW
42939 | Tms18 | 4 |  | unimplemented | RW
42940 | Hz18 | 4 |  | unimplemented | RW
42941 | Tms19 | 4 |  | unimplemented | RW
42942 | Hz19 | 4 |  | unimplemented | RW
42943 | Tms20 | 4 |  | unimplemented | RW
42944 | Hz20 | 4 |  | unimplemented | RW
42945 | CrvNam | 4 |  | unimplemented | RW
42953 | ReadOnly | 4 |  | supported | R

## 64257
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
42954 | ID |  |  | 64257
42955 | L |  |  | 370
42956 | ActCrv |  |  | supported | RW
42957 | ModEna |  |  | supported | RW
|  |  | ENABLED | supported
42958 | WinTms |  |  | unimplemented | RW
42959 | RvrtTms |  |  | unimplemented | RW
42960 | RmpTms |  |  | unimplemented | RW
42961 | NCrv |  |  | supported | R
42962 | NPt |  |  | supported | R
42963 | Tms_SF |  |  | -6 | R
42964 | Hz_SF |  |  | -2 | R
42965 | Pad |  |  |  | R
42966 | ActPt | 1 |  | supported | RW
42967 | Tms1 | 1 |  | supported | RW
42969 | Hz1 | 1 |  | supported | RW
42970 | Fn1 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42971 | Tms2 | 1 |  | supported | RW
42973 | Hz2 | 1 |  | supported | RW
42974 | Fn2 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42975 | Tms3 | 1 |  | supported | RW
42977 | Hz3 | 1 |  | supported | RW
42978 | Fn3 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42979 | Tms4 | 1 |  | supported | RW
42981 | Hz4 | 1 |  | supported | RW
42982 | Fn4 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42983 | Tms5 | 1 |  | supported | RW
42985 | Hz5 | 1 |  | supported | RW
42986 | Fn5 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42987 | Tms6 | 1 |  | supported | RW
42989 | Hz6 | 1 |  | supported | RW
42990 | Fn6 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42991 | Tms7 | 1 |  | supported | RW
42993 | Hz7 | 1 |  | supported | RW
42994 | Fn7 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42995 | Tms8 | 1 |  | supported | RW
42997 | Hz8 | 1 |  | supported | RW
42998 | Fn8 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
42999 | Tms9 | 1 |  | supported | RW
43001 | Hz9 | 1 |  | supported | RW
43002 | Fn9 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
43003 | Tms10 | 1 |  | supported | RW
43005 | Hz10 | 1 |  | supported | RW
43006 | Fn10 | 1 |  | supported | RW
|  |  | CEASE_TO_ENERGIZE | supported
43007 | Tms11 | 1 |  | unimplemented | RW
43009 | Hz11 | 1 |  | unimplemented | RW
43010 | Fn11 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
43011 | Tms12 | 1 |  | unimplemented | RW
43013 | Hz12 | 1 |  | unimplemented | RW
43014 | Fn12 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
43015 | Tms13 | 1 |  | unimplemented | RW
43017 | Hz13 | 1 |  | unimplemented | RW
43018 | Fn13 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
43019 | Tms14 | 1 |  | unimplemented | RW
43021 | Hz14 | 1 |  | unimplemented | RW
43022 | Fn14 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
43023 | Tms15 | 1 |  | unimplemented | RW
43025 | Hz15 | 1 |  | unimplemented | RW
43026 | Fn15 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
43027 | Tms16 | 1 |  | unimplemented | RW
43029 | Hz16 | 1 |  | unimplemented | RW
43030 | Fn16 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
43031 | Tms17 | 1 |  | unimplemented | RW
43033 | Hz17 | 1 |  | unimplemented | RW
43034 | Fn17 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
43035 | Tms18 | 1 |  | unimplemented | RW
43037 | Hz18 | 1 |  | unimplemented | RW
43038 | Fn18 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
43039 | Tms19 | 1 |  | unimplemented | RW
43041 | Hz19 | 1 |  | unimplemented | RW
43042 | Fn19 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
43043 | Tms20 | 1 |  | unimplemented | RW
43045 | Hz20 | 1 |  | unimplemented | RW
43046 | Fn20 | 1 |  | unimplemented | RW
|  |  | CEASE_TO_ENERGIZE | supported
43047 | CrvNam | 1 |  | unimplemented | RW
43055 | ReadOnly | 1 |  | supported | R
|  |  | READWRITE | supported
|  |  | READONLY | supported
43056 | ActPt | 2 |  | supported | RW
43057 | Tms1 | 2 |  | supported | RW
43059 | Hz1 | 2 |  | supported | RW
43060 | Fn1 | 2 |  | supported | RW
43061 | Tms2 | 2 |  | supported | RW
43063 | Hz2 | 2 |  | supported | RW
43064 | Fn2 | 2 |  | supported | RW
43065 | Tms3 | 2 |  | supported | RW
43067 | Hz3 | 2 |  | supported | RW
43068 | Fn3 | 2 |  | supported | RW
43069 | Tms4 | 2 |  | supported | RW
43071 | Hz4 | 2 |  | supported | RW
43072 | Fn4 | 2 |  | supported | RW
43073 | Tms5 | 2 |  | supported | RW
43075 | Hz5 | 2 |  | supported | RW
43076 | Fn5 | 2 |  | supported | RW
43077 | Tms6 | 2 |  | supported | RW
43079 | Hz6 | 2 |  | supported | RW
43080 | Fn6 | 2 |  | supported | RW
43081 | Tms7 | 2 |  | supported | RW
43083 | Hz7 | 2 |  | supported | RW
43084 | Fn7 | 2 |  | supported | RW
43085 | Tms8 | 2 |  | supported | RW
43087 | Hz8 | 2 |  | supported | RW
43088 | Fn8 | 2 |  | supported | RW
43089 | Tms9 | 2 |  | supported | RW
43091 | Hz9 | 2 |  | supported | RW
43092 | Fn9 | 2 |  | supported | RW
43093 | Tms10 | 2 |  | supported | RW
43095 | Hz10 | 2 |  | supported | RW
43096 | Fn10 | 2 |  | supported | RW
43097 | Tms11 | 2 |  | unimplemented | RW
43099 | Hz11 | 2 |  | unimplemented | RW
43100 | Fn11 | 2 |  | unimplemented | RW
43101 | Tms12 | 2 |  | unimplemented | RW
43103 | Hz12 | 2 |  | unimplemented | RW
43104 | Fn12 | 2 |  | unimplemented | RW
43105 | Tms13 | 2 |  | unimplemented | RW
43107 | Hz13 | 2 |  | unimplemented | RW
43108 | Fn13 | 2 |  | unimplemented | RW
43109 | Tms14 | 2 |  | unimplemented | RW
43111 | Hz14 | 2 |  | unimplemented | RW
43112 | Fn14 | 2 |  | unimplemented | RW
43113 | Tms15 | 2 |  | unimplemented | RW
43115 | Hz15 | 2 |  | unimplemented | RW
43116 | Fn15 | 2 |  | unimplemented | RW
43117 | Tms16 | 2 |  | unimplemented | RW
43119 | Hz16 | 2 |  | unimplemented | RW
43120 | Fn16 | 2 |  | unimplemented | RW
43121 | Tms17 | 2 |  | unimplemented | RW
43123 | Hz17 | 2 |  | unimplemented | RW
43124 | Fn17 | 2 |  | unimplemented | RW
43125 | Tms18 | 2 |  | unimplemented | RW
43127 | Hz18 | 2 |  | unimplemented | RW
43128 | Fn18 | 2 |  | unimplemented | RW
43129 | Tms19 | 2 |  | unimplemented | RW
43131 | Hz19 | 2 |  | unimplemented | RW
43132 | Fn19 | 2 |  | unimplemented | RW
43133 | Tms20 | 2 |  | unimplemented | RW
43135 | Hz20 | 2 |  | unimplemented | RW
43136 | Fn20 | 2 |  | unimplemented | RW
43137 | CrvNam | 2 |  | unimplemented | RW
43145 | ReadOnly | 2 |  | supported | R
43146 | ActPt | 3 |  | supported | RW
43147 | Tms1 | 3 |  | supported | RW
43149 | Hz1 | 3 |  | supported | RW
43150 | Fn1 | 3 |  | supported | RW
43151 | Tms2 | 3 |  | supported | RW
43153 | Hz2 | 3 |  | supported | RW
43154 | Fn2 | 3 |  | supported | RW
43155 | Tms3 | 3 |  | supported | RW
43157 | Hz3 | 3 |  | supported | RW
43158 | Fn3 | 3 |  | supported | RW
43159 | Tms4 | 3 |  | supported | RW
43161 | Hz4 | 3 |  | supported | RW
43162 | Fn4 | 3 |  | supported | RW
43163 | Tms5 | 3 |  | supported | RW
43165 | Hz5 | 3 |  | supported | RW
43166 | Fn5 | 3 |  | supported | RW
43167 | Tms6 | 3 |  | supported | RW
43169 | Hz6 | 3 |  | supported | RW
43170 | Fn6 | 3 |  | supported | RW
43171 | Tms7 | 3 |  | supported | RW
43173 | Hz7 | 3 |  | supported | RW
43174 | Fn7 | 3 |  | supported | RW
43175 | Tms8 | 3 |  | supported | RW
43177 | Hz8 | 3 |  | supported | RW
43178 | Fn8 | 3 |  | supported | RW
43179 | Tms9 | 3 |  | supported | RW
43181 | Hz9 | 3 |  | supported | RW
43182 | Fn9 | 3 |  | supported | RW
43183 | Tms10 | 3 |  | supported | RW
43185 | Hz10 | 3 |  | supported | RW
43186 | Fn10 | 3 |  | supported | RW
43187 | Tms11 | 3 |  | unimplemented | RW
43189 | Hz11 | 3 |  | unimplemented | RW
43190 | Fn11 | 3 |  | unimplemented | RW
43191 | Tms12 | 3 |  | unimplemented | RW
43193 | Hz12 | 3 |  | unimplemented | RW
43194 | Fn12 | 3 |  | unimplemented | RW
43195 | Tms13 | 3 |  | unimplemented | RW
43197 | Hz13 | 3 |  | unimplemented | RW
43198 | Fn13 | 3 |  | unimplemented | RW
43199 | Tms14 | 3 |  | unimplemented | RW
43201 | Hz14 | 3 |  | unimplemented | RW
43202 | Fn14 | 3 |  | unimplemented | RW
43203 | Tms15 | 3 |  | unimplemented | RW
43205 | Hz15 | 3 |  | unimplemented | RW
43206 | Fn15 | 3 |  | unimplemented | RW
43207 | Tms16 | 3 |  | unimplemented | RW
43209 | Hz16 | 3 |  | unimplemented | RW
43210 | Fn16 | 3 |  | unimplemented | RW
43211 | Tms17 | 3 |  | unimplemented | RW
43213 | Hz17 | 3 |  | unimplemented | RW
43214 | Fn17 | 3 |  | unimplemented | RW
43215 | Tms18 | 3 |  | unimplemented | RW
43217 | Hz18 | 3 |  | unimplemented | RW
43218 | Fn18 | 3 |  | unimplemented | RW
43219 | Tms19 | 3 |  | unimplemented | RW
43221 | Hz19 | 3 |  | unimplemented | RW
43222 | Fn19 | 3 |  | unimplemented | RW
43223 | Tms20 | 3 |  | unimplemented | RW
43225 | Hz20 | 3 |  | unimplemented | RW
43226 | Fn20 | 3 |  | unimplemented | RW
43227 | CrvNam | 3 |  | unimplemented | RW
43235 | ReadOnly | 3 |  | supported | R
43236 | ActPt | 4 |  | supported | RW
43237 | Tms1 | 4 |  | supported | RW
43239 | Hz1 | 4 |  | supported | RW
43240 | Fn1 | 4 |  | supported | RW
43241 | Tms2 | 4 |  | supported | RW
43243 | Hz2 | 4 |  | supported | RW
43244 | Fn2 | 4 |  | supported | RW
43245 | Tms3 | 4 |  | supported | RW
43247 | Hz3 | 4 |  | supported | RW
43248 | Fn3 | 4 |  | supported | RW
43249 | Tms4 | 4 |  | supported | RW
43251 | Hz4 | 4 |  | supported | RW
43252 | Fn4 | 4 |  | supported | RW
43253 | Tms5 | 4 |  | supported | RW
43255 | Hz5 | 4 |  | supported | RW
43256 | Fn5 | 4 |  | supported | RW
43257 | Tms6 | 4 |  | supported | RW
43259 | Hz6 | 4 |  | supported | RW
43260 | Fn6 | 4 |  | supported | RW
43261 | Tms7 | 4 |  | supported | RW
43263 | Hz7 | 4 |  | supported | RW
43264 | Fn7 | 4 |  | supported | RW
43265 | Tms8 | 4 |  | supported | RW
43267 | Hz8 | 4 |  | supported | RW
43268 | Fn8 | 4 |  | supported | RW
43269 | Tms9 | 4 |  | supported | RW
43271 | Hz9 | 4 |  | supported | RW
43272 | Fn9 | 4 |  | supported | RW
43273 | Tms10 | 4 |  | supported | RW
43275 | Hz10 | 4 |  | supported | RW
43276 | Fn10 | 4 |  | supported | RW
43277 | Tms11 | 4 |  | unimplemented | RW
43279 | Hz11 | 4 |  | unimplemented | RW
43280 | Fn11 | 4 |  | unimplemented | RW
43281 | Tms12 | 4 |  | unimplemented | RW
43283 | Hz12 | 4 |  | unimplemented | RW
43284 | Fn12 | 4 |  | unimplemented | RW
43285 | Tms13 | 4 |  | unimplemented | RW
43287 | Hz13 | 4 |  | unimplemented | RW
43288 | Fn13 | 4 |  | unimplemented | RW
43289 | Tms14 | 4 |  | unimplemented | RW
43291 | Hz14 | 4 |  | unimplemented | RW
43292 | Fn14 | 4 |  | unimplemented | RW
43293 | Tms15 | 4 |  | unimplemented | RW
43295 | Hz15 | 4 |  | unimplemented | RW
43296 | Fn15 | 4 |  | unimplemented | RW
43297 | Tms16 | 4 |  | unimplemented | RW
43299 | Hz16 | 4 |  | unimplemented | RW
43300 | Fn16 | 4 |  | unimplemented | RW
43301 | Tms17 | 4 |  | unimplemented | RW
43303 | Hz17 | 4 |  | unimplemented | RW
43304 | Fn17 | 4 |  | unimplemented | RW
43305 | Tms18 | 4 |  | unimplemented | RW
43307 | Hz18 | 4 |  | unimplemented | RW
43308 | Fn18 | 4 |  | unimplemented | RW
43309 | Tms19 | 4 |  | unimplemented | RW
43311 | Hz19 | 4 |  | unimplemented | RW
43312 | Fn19 | 4 |  | unimplemented | RW
43313 | Tms20 | 4 |  | unimplemented | RW
43315 | Hz20 | 4 |  | unimplemented | RW
43316 | Fn20 | 4 |  | unimplemented | RW
43317 | CrvNam | 4 |  | unimplemented | RW
43325 | ReadOnly | 4 |  | supported | R

## 145
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
43326 | ID |  |  | 145
43327 | L |  |  | 8
43328 | Ramp Up Rate (NomRmpUpRte) |  |  | supported | RW
43329 | NomRmpDnRte |  |  | supported | RW
43330 | Emergency Ramp Up Rate (EmgRmpUpRte) |  |  | unimplemented | RW
43331 | Emergency Ramp Down Rate (EmgRmpDnRte) |  |  | unimplemented | RW
43332 | Connect Ramp Up Rate (ConnRmpUpRte) |  |  | supported | RW
43333 | Connect Ramp Down Rate (ConnRmpDnRte) |  |  | unimplemented | RW
43334 | Default Ramp Rate (AGra) |  |  | unimplemented | RW
43335 | Ramp Rate Scale Factor (Rmp_SF) |  |  | -1 | R

## 64203
Address | Point | Index | Subvalue | Value | R/W | Conformance Notes
43336 | ID |  |  | 64203
43337 | L |  |  | 12
43338 | ModEna |  |  | supported | RW
|  |  | DISABLE | supported
|  |  | ENABLE | supported
43339 | ReConn_Tms |  |  | supported | RW
43340 | ReConnMinV |  |  | supported | RW
43341 | ReConnMaxV |  |  | supported | RW
43342 | ReConnMinHz |  |  | supported | RW
43343 | ReConnMaxHz |  |  | supported | RW
43344 | VoltWattLatchTime (VWLatchTms) |  |  | supported | RW
43345 | FreqWattLatchTime (FWLatchTms) |  |  | supported | RW
43346 | Tms_SF |  |  | 0 | R
43347 | V_SF |  |  | -1 | R
43348 | Hz_SF |  |  | -2 | R
43349 | Pad |  |  |  | R