## Index
Model | Label | Description | Notes
1 | Common | Make, model and serial number information for this device
102 | Inverter (Split-Phase) | Include this model for split phase inverter monitoring
120 | Nameplate | Inverter Controls Nameplate Ratings | Ref 3: 8.14.3.2, Ref 4: 17
123 | Immediate Controls | Immediate Inverter Controls | Ref 3: 8.7.1.2, 8.7.2.2, 8.7.3.2
126 | Static Volt-VAR | Static Volt-VAR Arrays | Ref 3: 8.8.1.2
129 | LVRTD | LVRT Must Disconnect | Ref 4: 11
130 | HVRTD | HVRT Must Disconnect | Ref 4: 11
132 | Volt-Watt | Volt-Watt | Ref 3: 8.12.1.2
134 | Freq-Watt Crv | Curve-Based Frequency-Watt | Ref 3: 8.9.1.2, 8.9.4.2
135 | LFRT | Low Frequency Ride-through | Ref 4: 11
145 | Extended Settings | Inverter controls extended settings
64202 | Pika Energy Inverter Arbitrage Control | Power control model for Energy Island
64203 | Pika Energy Reconnect Control | Define grid parameters required for reconnection
64204 | Inverter Export | Grid export measurements for inverters with current transducers
64205 | Utility Compliance Configuration | Configure inverter settings based on utility requirements
64206 | Energy Island Configuration | Configure Energy Island system settings
64207 | REbus Status | REbus status data that is defined commonly across Pika Energy REbus devices
64208 | Inverter Status | Miscellaneous Pika Energy inverter status registers
64254 | LVRTD | LVRT Must Disconnect | Ref 4: 11
64255 | HVRTD | HVRT Must Disconnect | Ref 4: 11
64256 | LFRT | Low Frequency Ride-through | Ref 4: 11
64257 | HFRT | High Frequency Ride-through | Ref 4: 11

## 1
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Common | 1 | uint16 |  |  | R | M | Make, model and serial number information for this device
Header |  | 1 |  | 1 | L |  | 66 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 16 | Mn | Manufacturer |  | string |  |  | R | M | Well known value registered with SunSpec for compliance
Fixed Block |  | 18 | 16 | 16 | Md | Model |  | string |  |  | R | M | Manufacturer specific value (32 chars)
Fixed Block |  | 34 | 32 | 8 | Opt | Options |  | string |  |  | R | O | Manufacturer specific value (16 chars)
Fixed Block |  | 42 | 40 | 8 | Vr | Version |  | string |  |  | R | O | Manufacturer specific value (16 chars)
Fixed Block |  | 50 | 48 | 16 | SN | Serial Number |  | string |  |  | R | M | Manufacturer specific value (32 chars)
Fixed Block |  | 66 | 64 | 1 | DA | Device Address |  | uint16 |  |  | RW | O | Modbus device address
Fixed Block |  | 67 | 65 | Size: 1; Name: Pad; Type: pad; R/W: R | O | Force even alignment

## 102
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inverter (Split-Phase) | 102 | uint16 |  |  | R | M | Include this model for split phase inverter monitoring
Header |  | 1 |  | 1 | L |  | 50 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | A | Amps |  | uint16 | A | A_SF | R | M | AC Current | Sum of active phases
Fixed Block |  | 3 | 1 | 1 | AphA | Amps PhaseA |  | uint16 | A | A_SF | R | M | Phase A Current | Connected Phase
Fixed Block |  | 4 | 2 | 1 | AphB | Amps PhaseB |  | uint16 | A | A_SF | R | M | Phase B Current | Connected Phase
Fixed Block |  | 5 | 3 | 1 | AphC | Amps PhaseC |  | uint16 | A | A_SF | R | O | Phase C Current
Fixed Block |  | 6 | 4 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 7 | 5 | 1 | PPVphAB | Phase Voltage AB |  | uint16 | V | V_SF | R | O | Phase Voltage AB
Fixed Block |  | 8 | 6 | 1 | PPVphBC | Phase Voltage BC |  | uint16 | V | V_SF | R | O | Phase Voltage BC
Fixed Block |  | 9 | 7 | 1 | PPVphCA | Phase Voltage CA |  | uint16 | V | V_SF | R | O | Phase Voltage CA
Fixed Block |  | 10 | 8 | 1 | PhVphA | Phase Voltage AN |  | uint16 | V | V_SF | R | M | Phase Voltage AN
Fixed Block |  | 11 | 9 | 1 | PhVphB | Phase Voltage BN |  | uint16 | V | V_SF | R | M | Phase Voltage BN
Fixed Block |  | 12 | 10 | 1 | PhVphC | Phase Voltage CN |  | uint16 | V | V_SF | R | O | Phase Voltage CN
Fixed Block |  | 13 | 11 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 14 | 12 | 1 | W | Watts |  | int16 | W | W_SF | R | M | AC Power
Fixed Block |  | 15 | 13 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 16 | 14 | 1 | Hz | Hz |  | uint16 | Hz | Hz_SF | R | M | Line Frequency
Fixed Block |  | 17 | 15 | Size: 1; Name: Hz_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 18 | 16 | 1 | VA | VA |  | int16 | VA | VA_SF | R | O | AC Apparent Power
Fixed Block |  | 19 | 17 | Size: 1; Name: VA_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 20 | 18 | 1 | VAr | VAr |  | int16 | var | VAr_SF | R | O | AC Reactive Power
Fixed Block |  | 21 | 19 | Size: 1; Name: VAr_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 22 | 20 | 1 | PF | PF |  | int16 | Pct | PF_SF | R | O | AC Power Factor
Fixed Block |  | 23 | 21 | Size: 1; Name: PF_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 24 | 22 | 2 | WH | WattHours |  | acc32 | Wh | WH_SF | R | M | AC Energy
Fixed Block |  | 26 | 24 | Size: 1; Name: WH_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 27 | 25 | 1 | DCA | DC Amps |  | uint16 | A | DCA_SF | R | O | DC Current
Fixed Block |  | 28 | 26 | Size: 1; Name: DCA_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 29 | 27 | 1 | DCV | DC Voltage |  | uint16 | V | DCV_SF | R | O | DC Voltage
Fixed Block |  | 30 | 28 | Size: 1; Name: DCV_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 31 | 29 | 1 | DCW | DC Watts |  | int16 | W | DCW_SF | R | O | DC Power
Fixed Block |  | 32 | 30 | Size: 1; Name: DCW_SF; Type: sunssf; R/W: R | O
Fixed Block |  | 33 | 31 | 1 | TmpCab | Cabinet Temperature |  | int16 | C | Tmp_SF | R | M | Cabinet Temperature
Fixed Block |  | 34 | 32 | 1 | TmpSnk | Heat Sink Temperature |  | int16 | C | Tmp_SF | R | O | Heat Sink Temperature
Fixed Block |  | 35 | 33 | 1 | TmpTrns | Transformer Temperature |  | int16 | C | Tmp_SF | R | O | Transformer Temperature
Fixed Block |  | 36 | 34 | 1 | TmpOt | Other Temperature |  | int16 | C | Tmp_SF | R | O | Other Temperature
Fixed Block |  | 37 | 35 | Size: 1; Name: Tmp_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 38 | 36 | 1 | St | Operating State |  | enum16 |  |  | R | M | Enumerated value. Operating state
Fixed Block |  | 39 | 37 | 1 | StVnd | Vendor Operating State |  | enum16 |  |  | R | O | Vendor specific operating state code
Fixed Block |  | 40 | 38 | 2 | Evt1 | Event1 |  | bitfield32 |  |  | R | M | Bitmask value. Event fields
Fixed Block |  | 42 | 40 | 2 | Evt2 | Event Bitfield 2 |  | bitfield32 |  |  | R | M | Reserved for future use
Fixed Block |  | 44 | 42 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 46 | 44 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 48 | 46 | 2 | EvtVnd3 | Vendor Event Bitfield 3 |  | bitfield32 |  |  | R | O | Vendor defined events
Fixed Block |  | 50 | 48 | 2 | EvtVnd4 | Vendor Event Bitfield 4 |  | bitfield32 |  |  | R | O | Vendor defined events
enum16 | St |  |  | Name: OFF; Label: Off; Value: 1 |  | Device is not operating
enum16 | St |  |  | Name: SLEEPING; Label: Sleeping; Value: 2 |  | Device is sleeping / auto-shudown
enum16 | St |  |  | Name: STARTING; Label: Starting; Value: 3 |  | Device is staring up
enum16 | St |  |  | Name: MPPT; Label: MPPT; Value: 4 |  | Device is auto tracking maximum power point
enum16 | St |  |  | Name: THROTTLED; Label: Throttled; Value: 5 |  | Device is operating at reduced power output
enum16 | St |  |  | Name: SHUTTING_DOWN; Label: Shutting down; Value: 6 |  | Device is shutting down
enum16 | St |  |  | Name: FAULT; Label: Fault; Value: 7 |  | One or more faults exist
enum16 | St |  |  | Name: STANDBY; Label: Standby; Value: 8 |  | Device is in standby mode
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground fault; Value: 0
bitfield32 | Evt1 |  |  | Name: DC_OVER_VOLT; Label: DC over voltage; Value: 1
bitfield32 | Evt1 |  |  | Name: AC_DISCONNECT; Label: AC disconnect open; Value: 2
bitfield32 | Evt1 |  |  | Name: DC_DISCONNECT; Label: DC disconnect open; Value: 3
bitfield32 | Evt1 |  |  | Name: GRID_DISCONNECT; Label: Grid shutdown; Value: 4
bitfield32 | Evt1 |  |  | Name: CABINET_OPEN; Label: Cabinet open; Value: 5
bitfield32 | Evt1 |  |  | Name: MANUAL_SHUTDOWN; Label: Manual shutdown; Value: 6
bitfield32 | Evt1 |  |  | Name: OVER_TEMP; Label: Over temperature; Value: 7
bitfield32 | Evt1 |  |  | Name: OVER_FREQUENCY; Label: Frequency above limit; Value: 8
bitfield32 | Evt1 |  |  | Name: UNDER_FREQUENCY; Label: Frequency under limit; Value: 9
bitfield32 | Evt1 |  |  | Name: AC_OVER_VOLT; Label: AC Voltage above limit; Value: 10
bitfield32 | Evt1 |  |  | Name: AC_UNDER_VOLT; Label: AC Voltage under limit; Value: 11
bitfield32 | Evt1 |  |  | Name: BLOWN_STRING_FUSE; Label: Blown String fuse on input; Value: 12
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP; Label: Under temperature; Value: 13
bitfield32 | Evt1 |  |  | Name: MEMORY_LOSS; Label: Generic Memory or Communication error (internal); Value: 14
bitfield32 | Evt1 |  |  | Name: HW_TEST_FAILURE; Label: Hardware test failure; Value: 15

## 120
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Nameplate | 120 | uint16 |  |  | R | M | Inverter Controls Nameplate Ratings | Ref 3: 8.14.3.2, Ref 4: 17
Header |  | 1 |  | 1 | L |  | 26 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | DERTyp | DERTyp |  | enum16 |  |  | R | M | Type of DER device. Default value is 4 to indicate PV device.
Fixed Block |  | 3 | 1 | 1 | WRtg | WRtg |  | uint16 | W | WRtg_SF | R | M | Continuous power output capability of the inverter.
Fixed Block |  | 4 | 2 | 1 | WRtg_SF | WRtg_SF |  | sunssf |  |  | R | M | Scale factor
Fixed Block |  | 5 | 3 | 1 | VARtg | VARtg |  | uint16 | VA | VARtg_SF | R | M | Continuous Volt-Ampere capability of the inverter.
Fixed Block |  | 6 | 4 | 1 | VARtg_SF | VARtg_SF |  | sunssf |  |  | R | M | Scale factor
Fixed Block |  | 7 | 5 | 1 | VArRtgQ1 | VArRtgQ1 |  | int16 | var | VArRtg_SF | R | M | Continuous VAR capability of the inverter in quadrant 1.
Fixed Block |  | 8 | 6 | 1 | VArRtgQ2 | VArRtgQ2 |  | int16 | var | VArRtg_SF | R | M | Continuous VAR capability of the inverter in quadrant 2.
Fixed Block |  | 9 | 7 | 1 | VArRtgQ3 | VArRtgQ3 |  | int16 | var | VArRtg_SF | R | M | Continuous VAR capability of the inverter in quadrant 3.
Fixed Block |  | 10 | 8 | 1 | VArRtgQ4 | VArRtgQ4 |  | int16 | var | VArRtg_SF | R | M | Continuous VAR capability of the inverter in quadrant 4.
Fixed Block |  | 11 | 9 | 1 | VArRtg_SF | VArRtg_SF |  | sunssf |  |  | R | M | Scale factor
Fixed Block |  | 12 | 10 | 1 | ARtg | ARtg |  | uint16 | A | ARtg_SF | R | M | Maximum RMS AC current level capability of the inverter. | Sum of all connected phases. Current rating under nominal voltage under nominal power factor.
Fixed Block |  | 13 | 11 | 1 | ARtg_SF | ARtg_SF |  | sunssf |  |  | R | M | Scale factor
Fixed Block |  | 14 | 12 | 1 | PFRtgQ1 | PFRtgQ1 |  | int16 | cos() | PFRtg_SF | R | M | Minimum power factor capability of the inverter in quadrant 1. | EEI sign convention.
Fixed Block |  | 15 | 13 | 1 | PFRtgQ2 | PFRtgQ2 |  | int16 | cos() | PFRtg_SF | R | M | Minimum power factor capability of the inverter in quadrant 2. | EEI sign convention.
Fixed Block |  | 16 | 14 | 1 | PFRtgQ3 | PFRtgQ3 |  | int16 | cos() | PFRtg_SF | R | M | Minimum power factor capability of the inverter in quadrant 3. | EEI sign convention.
Fixed Block |  | 17 | 15 | 1 | PFRtgQ4 | PFRtgQ4 |  | int16 | cos() | PFRtg_SF | R | M | Minimum power factor capability of the inverter in quadrant 4. | EEI sign convention.
Fixed Block |  | 18 | 16 | 1 | PFRtg_SF | PFRtg_SF |  | sunssf |  |  | R | M | Scale factor
Fixed Block |  | 19 | 17 | 1 | WHRtg | WHRtg |  | uint16 | Wh | WHRtg_SF | R | O | Nominal energy rating of storage device.
Fixed Block |  | 20 | 18 | 1 | WHRtg_SF | WHRtg_SF |  | sunssf |  |  | R | O | Scale factor
Fixed Block |  | 21 | 19 | 1 | AhrRtg | AhrRtg |  | uint16 | AH | AhrRtg_SF | R | O | The useable capacity of the battery. Maximum charge minus minimum charge from a technology capability perspective (Amp-hour capacity rating).
Fixed Block |  | 22 | 20 | 1 | AhrRtg_SF | AhrRtg_SF |  | sunssf |  |  | R | O | Scale factor for amp-hour rating.
Fixed Block |  | 23 | 21 | 1 | MaxChaRte | MaxChaRte |  | uint16 | W | MaxChaRte_SF | R | O | Maximum rate of energy transfer into the storage device.
Fixed Block |  | 24 | 22 | 1 | MaxChaRte_SF | MaxChaRte_SF |  | sunssf |  |  | R | O | Scale factor
Fixed Block |  | 25 | 23 | 1 | MaxDisChaRte | MaxDisChaRte |  | uint16 | W | MaxDisChaRte_SF | R | O | Maximum rate of energy transfer out of the storage device.
Fixed Block |  | 26 | 24 | 1 | MaxDisChaRte_SF | MaxDisChaRte_SF |  | sunssf |  |  | R | O | Scale factor
Fixed Block |  | 27 | 25 | 1 | Pad | Pad |  | pad |  |  | R | O | Pad register.
enum16 | DERTyp |  |  | Name: PV; Value: 4
enum16 | DERTyp |  |  | Name: PV_STOR; Value: 82

## 123
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Immediate Controls | 123 | uint16 |  |  | R | M | Immediate Inverter Controls | Ref 3: 8.7.1.2, 8.7.2.2, 8.7.3.2
Header |  | 1 |  | 1 | L |  | 24 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Conn_WinTms | Conn_WinTms |  | uint16 | Secs |  | RW | O | Time window for connect/disconnect.
Fixed Block |  | 3 | 1 | 1 | Conn_RvrtTms | Conn_RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for connect/disconnect.
Fixed Block |  | 4 | 2 | 1 | Conn | Conn |  | enum16 |  |  | RW | M | Enumerated valued. Connection control.
Fixed Block |  | 5 | 3 | 1 | WMaxLimPct | WMaxLimPct |  | uint16 | % WMax | WMaxLimPct_SF | RW | M | Set power output to specified level.
Fixed Block |  | 6 | 4 | 1 | WMaxLimPct_WinTms | WMaxLimPct_WinTms |  | uint16 | Secs |  | RW | O | Time window for power limit change.
Fixed Block |  | 7 | 5 | 1 | WMaxLimPct_RvrtTms | WMaxLimPct_RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for power limit.
Fixed Block |  | 8 | 6 | 1 | WMaxLimPct_RmpTms | WMaxLimPct_RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current setpoint to new setpoint.
Fixed Block |  | 9 | 7 | 1 | WMaxLim_Ena | WMaxLim_Ena |  | enum16 |  |  | RW | M | Enumerated valued. Throttle enable/disable control.
Fixed Block |  | 10 | 8 | 1 | OutPFSet | OutPFSet |  | int16 | cos() | OutPFSet_SF | RW | M | Set power factor to specific value - cosine of angle.
Fixed Block |  | 11 | 9 | 1 | OutPFSet_WinTms | OutPFSet_WinTms |  | uint16 | Secs |  | RW | O | Time window for power factor change.
Fixed Block |  | 12 | 10 | 1 | OutPFSet_RvrtTms | OutPFSet_RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for power factor.
Fixed Block |  | 13 | 11 | 1 | OutPFSet_RmpTms | OutPFSet_RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current setpoint to new setpoint.
Fixed Block |  | 14 | 12 | 1 | OutPFSet_Ena | OutPFSet_Ena |  | enum16 |  |  | RW | M | Enumerated valued. Fixed power factor enable/disable control.
Fixed Block |  | 15 | 13 | 1 | VArWMaxPct | VArWMaxPct |  | int16 | % WMax | VArPct_SF | RW | O | Reactive power in percent of WMax.
Fixed Block |  | 16 | 14 | 1 | VArMaxPct | VArMaxPct |  | int16 | % VArMax | VArPct_SF | RW | O | Reactive power in percent of VArMax.
Fixed Block |  | 17 | 15 | 1 | VArAvalPct | VArAvalPct |  | int16 | % VArAval | VArPct_SF | RW | O | Reactive power in percent of VArAval.
Fixed Block |  | 18 | 16 | 1 | VArPct_WinTms | VArPct_WinTms |  | uint16 | Secs |  | RW | O | Time window for VAR limit change.
Fixed Block |  | 19 | 17 | 1 | VArPct_RvrtTms | VArPct_RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for VAR limit.
Fixed Block |  | 20 | 18 | 1 | VArPct_RmpTms | VArPct_RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current setpoint to new setpoint.
Fixed Block |  | 21 | 19 | 1 | VArPct_Mod | VArPct_Mod |  | enum16 |  |  | RW | O | Enumerated value. VAR percent limit mode.
Fixed Block |  | 22 | 20 | 1 | VArPct_Ena | VArPct_Ena |  | enum16 |  |  | RW | M | Enumerated valued. Percent limit VAr enable/disable control.
Fixed Block |  | 23 | 21 | 1 | WMaxLimPct_SF | WMaxLimPct_SF |  | sunssf |  |  | R | M | Scale factor for power output percent.
Fixed Block |  | 24 | 22 | 1 | OutPFSet_SF | OutPFSet_SF |  | sunssf |  |  | R | M | Scale factor for power factor.
Fixed Block |  | 25 | 23 | 1 | VArPct_SF | VArPct_SF |  | sunssf |  |  | R | O | Scale factor for reactive power percent.
enum16 | Conn |  |  | Name: DISCONNECT; Value: 0
enum16 | Conn |  |  | Name: CONNECT; Value: 1
enum16 | WMaxLim_Ena |  |  | Name: DISABLED; Value: 0
enum16 | WMaxLim_Ena |  |  | Name: ENABLED; Value: 1
enum16 | OutPFSet_Ena |  |  | Name: DISABLED; Value: 0
enum16 | OutPFSet_Ena |  |  | Name: ENABLED; Value: 1
enum16 | VArPct_Mod |  |  | Name: NONE; Value: 0 |  | No VAR limit
enum16 | VArPct_Mod |  |  | Name: WMax; Value: 1 |  | VAR limit as a % of Wmax
enum16 | VArPct_Mod |  |  | Name: VArMax; Value: 2 |  | VAR limit as a % of VArMax
enum16 | VArPct_Mod |  |  | Name: VArAval; Value: 3 |  | VAR limit as a % of VArAval
enum16 | VArPct_Ena |  |  | Name: DISABLED; Value: 0
enum16 | VArPct_Ena |  |  | Name: ENABLED; Value: 1

## 126
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Static Volt-VAR | 126 | uint16 |  |  | R | M | Static Volt-VAR Arrays | Ref 3: 8.8.1.2
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 54) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is Volt-VAR control active.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for volt-VAR change.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for volt-VAR curve selection.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | The time of the PT1 in seconds (time to accomplish a change of 95%).
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximum of 20).
Fixed Block |  | 9 | 7 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 10 | 8 | 1 | DeptRef_SF | DeptRef_SF |  | sunssf |  |  | R | M | scale factor for dependent variable.
Fixed Block |  | 11 | 9 | 1 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | R | O | Scale factor for increment and decrement ramps.
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | DeptRef | DeptRef |  | enum16 |  |  | RW | M | Meaning of dependent variable: 1=%WMax 2=%VArMax 3=%VArAval.
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 Volts.
Repeating Block |  | 15 | 3 | 1 | VAr1 | VAr1 |  | int16 |  | DeptRef_SF | RW | M | Point 1 VARs.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 Volts.
Repeating Block |  | 17 | 5 | 1 | VAr2 | VAr2 |  | int16 |  | DeptRef_SF | RW | O | Point 2 VARs.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 2 Volts.
Repeating Block |  | 19 | 7 | 1 | VAr3 | VAr3 |  | int16 | Various | DeptRef_SF | RW | O | Point 3 VARs.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 |  | V_SF | RW | O | Point 4 Volts.
Repeating Block |  | 21 | 9 | 1 | VAr4 | VAr4 |  | int16 |  | DeptRef_SF | RW | O | Point 4 VARs.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 Volts.
Repeating Block |  | 23 | 11 | 1 | VAr5 | VAr5 |  | int16 |  | DeptRef_SF | RW | O | Point 5 VARs.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 Volts.
Repeating Block |  | 25 | 13 | 1 | VAr6 | VAr6 |  | int16 |  | DeptRef_SF | RW | O | Point 6 VARs.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 Volts.
Repeating Block |  | 27 | 15 | 1 | VAr7 | VAr7 |  | int16 |  | DeptRef_SF | RW | O | Point 7 VARs.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 Volts.
Repeating Block |  | 29 | 17 | 1 | VAr8 | VAr8 |  | int16 |  | DeptRef_SF | RW | O | Point 8 VARs.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 Volts.
Repeating Block |  | 31 | 19 | 1 | VAr9 | VAr9 |  | int16 |  | DeptRef_SF | RW | O | Point 9 VARs.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 Volts.
Repeating Block |  | 33 | 21 | 1 | VAr10 | VAr10 |  | int16 |  | DeptRef_SF | RW | O | Point 10 VARs.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 Volts.
Repeating Block |  | 35 | 23 | 1 | VAr11 | VAr11 |  | int16 |  | DeptRef_SF | RW | O | Point 11 VARs.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 Volts.
Repeating Block |  | 37 | 25 | 1 | VAr12 | VAr12 |  | int16 |  | DeptRef_SF | RW | O | Point 12 VARs.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 Volts.
Repeating Block |  | 39 | 27 | 1 | VAr13 | VAr13 |  | int16 |  | DeptRef_SF | RW | O | Point 13 VARs.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 Volts.
Repeating Block |  | 41 | 29 | 1 | VAr14 | VAr14 |  | int16 |  | DeptRef_SF | RW | O | Point 14 VARs.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 Volts.
Repeating Block |  | 43 | 31 | 1 | VAr15 | VAr15 |  | int16 |  | DeptRef_SF | RW | O | Point 15 VARs.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 Volts.
Repeating Block |  | 45 | 33 | 1 | VAr16 | VAr16 |  | int16 |  | DeptRef_SF | RW | O | Point 16 VARs.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 Volts.
Repeating Block |  | 47 | 35 | 1 | VAr17 | VAr17 |  | int16 |  | DeptRef_SF | RW | O | Point 17 VARs.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 Volts.
Repeating Block |  | 49 | 37 | 1 | VAr18 | VAr18 |  | int16 |  | DeptRef_SF | RW | O | Point 18 VARs.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 Volts.
Repeating Block |  | 51 | 39 | 1 | VAr19 | VAr19 |  | int16 |  | DeptRef_SF | RW | O | Point 19 VARs.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 Volts.
Repeating Block |  | 53 | 41 | 1 | VAr20 | VAr20 |  | int16 |  | DeptRef_SF | RW | O | Point 20 VARs.
Repeating Block |  | 54 | 42 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve. (Max 16 chars)
Repeating Block |  | 62 | 50 | 1 | RmpTms |  |  | uint16 | Secs |  | RW | O
Repeating Block |  | 63 | 51 | 1 | RmpDecTmm | RmpDecTmm |  | uint16 | % ref_value/min | RmpIncDec_SF | RW | O | The maximum rate at which the VAR value may be reduced in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
Repeating Block |  | 64 | 52 | 1 | RmpIncTmm | RmpIncTmm |  | uint16 | % ref_value/min | RmpIncDec_SF | RW | O | The maximum rate at which the VAR value may be increased in response to changes in the voltage value. %refVal is %WMax %VArMax or %VArAval depending on value of DeptRef.
Repeating Block |  | 65 | 53 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Boolean flag indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | DeptRef |  |  | Name: WMax; Value: 1
enum16 | DeptRef |  |  | Name: VArMax; Value: 2
enum16 | DeptRef |  |  | Name: VArAval; Value: 3
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 129
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | LVRTD | 129 | uint16 |  |  | R | M | LVRT Must Disconnect | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | LVRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for LVRT change. | Setting is ignored for LVRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for LVRT curve selection. | Setting is ignored for LVRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for LVRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 must disconnect duration.
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 must disconnect voltage.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 must disconnect duration.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 must disconnect voltage.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 must disconnect duration.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 3 must disconnect voltage.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 must disconnect duration.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 | % VRef | V_SF | RW | O | Point 4 must disconnect voltage.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 must disconnect duration.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 must disconnect voltage.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 must disconnect duration.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 must disconnect voltage.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 must disconnect duration.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 must disconnect voltage.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 must disconnect duration.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 must disconnect voltage.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 must disconnect duration.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 must disconnect voltage.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 must disconnect duration.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 must disconnect voltage.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 must disconnect duration.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 must disconnect voltage.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 must disconnect duration.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 must disconnect voltage.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 must disconnect duration.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 must disconnect voltage.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 must disconnect duration.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 must disconnect voltage.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 must disconnect duration.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 must disconnect voltage.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 must disconnect duration.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 must disconnect voltage.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 must disconnect duration.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 must disconnect voltage.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 must disconnect duration.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 must disconnect voltage.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 must disconnect duration.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 must disconnect voltage.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 must disconnect duration.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 must disconnect voltage.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 130
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | HVRTD | 130 | uint16 |  |  | R | M | HVRT Must Disconnect | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | HVRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for HVRT change. | Setting is ignored for HVRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for HVRT curve selection. | Setting is ignored for HVRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for HVRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 must disconnect duration.
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 must disconnect voltage.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 must disconnect duration.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 must disconnect voltage.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 must disconnect duration.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 3 must disconnect voltage.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 must disconnect duration.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 | % VRef | V_SF | RW | O | Point 4 must disconnect voltage.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 must disconnect duration.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 must disconnect voltage.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 must disconnect duration.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 must disconnect voltage.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 must disconnect duration.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 must disconnect voltage.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 must disconnect duration.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 must disconnect voltage.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 must disconnect duration.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 must disconnect voltage.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 must disconnect duration.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 must disconnect voltage.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 must disconnect duration.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 must disconnect voltage.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 must disconnect duration.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 must disconnect voltage.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 must disconnect duration.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 must disconnect voltage.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 must disconnect duration.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 must disconnect voltage.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 must disconnect duration.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 must disconnect voltage.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 must disconnect duration.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 must disconnect voltage.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 must disconnect duration.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 must disconnect voltage.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 must disconnect duration.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 must disconnect voltage.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 must disconnect duration.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 must disconnect voltage.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 must disconnect duration.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 must disconnect voltage.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 132
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Volt-Watt | 132 | uint16 |  |  | R | M | Volt-Watt | Ref 3: 8.12.1.2
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 54) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is Volt-Watt control active.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for volt-watt change.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for volt-watt curve selection.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend min. 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of points in array (maximum 20).
Fixed Block |  | 9 | 7 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 10 | 8 | 1 | DeptRef_SF | DeptRef_SF |  | sunssf |  |  | R | M | Scale Factor for % DeptRef
Fixed Block |  | 11 | 9 | 1 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf |  |  | R | O | Scale factor for increment and decrement ramps.
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | DeptRef | DeptRef |  | enum16 |  |  | RW | M | Defines the meaning of the Watts DeptRef. 1=% WMax 2=% WAvail
Repeating Block |  | 14 | 2 | 1 | V1 | V1 |  | uint16 | % VRef | V_SF | RW | M | Point 1 Volts.
Repeating Block |  | 15 | 3 | 1 | W1 | W1 |  | int16 | % VRef | DeptRef_SF | RW | M | Point 1 Watts.
Repeating Block |  | 16 | 4 | 1 | V2 | V2 |  | uint16 | % VRef | V_SF | RW | O | Point 2 Volts.
Repeating Block |  | 17 | 5 | 1 | W2 | W2 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 2 Watts.
Repeating Block |  | 18 | 6 | 1 | V3 | V3 |  | uint16 | % VRef | V_SF | RW | O | Point 3 Volts.
Repeating Block |  | 19 | 7 | 1 | W3 | W3 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 3 Watts.
Repeating Block |  | 20 | 8 | 1 | V4 | V4 |  | uint16 | % VRef | V_SF | RW | O | Point 4 Volts.
Repeating Block |  | 21 | 9 | 1 | W4 | W4 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 4 Watts.
Repeating Block |  | 22 | 10 | 1 | V5 | V5 |  | uint16 | % VRef | V_SF | RW | O | Point 5 Volts.
Repeating Block |  | 23 | 11 | 1 | W5 | W5 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 5 Watts.
Repeating Block |  | 24 | 12 | 1 | V6 | V6 |  | uint16 | % VRef | V_SF | RW | O | Point 6 Volts.
Repeating Block |  | 25 | 13 | 1 | W6 | W6 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 6 Watts.
Repeating Block |  | 26 | 14 | 1 | V7 | V7 |  | uint16 | % VRef | V_SF | RW | O | Point 7 Volts.
Repeating Block |  | 27 | 15 | 1 | W7 | W7 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 7 Watts.
Repeating Block |  | 28 | 16 | 1 | V8 | V8 |  | uint16 | % VRef | V_SF | RW | O | Point 8 Volts.
Repeating Block |  | 29 | 17 | 1 | W8 | W8 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 8 Watts.
Repeating Block |  | 30 | 18 | 1 | V9 | V9 |  | uint16 | % VRef | V_SF | RW | O | Point 9 Volts.
Repeating Block |  | 31 | 19 | 1 | W9 | W9 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 9 Watts.
Repeating Block |  | 32 | 20 | 1 | V10 | V10 |  | uint16 | % VRef | V_SF | RW | O | Point 10 Volts.
Repeating Block |  | 33 | 21 | 1 | W10 | W10 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 10 Watts.
Repeating Block |  | 34 | 22 | 1 | V11 | V11 |  | uint16 | % VRef | V_SF | RW | O | Point 11 Volts.
Repeating Block |  | 35 | 23 | 1 | W11 | W11 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 11 Watts.
Repeating Block |  | 36 | 24 | 1 | V12 | V12 |  | uint16 | % VRef | V_SF | RW | O | Point 12 Volts.
Repeating Block |  | 37 | 25 | 1 | W12 | W12 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 12 Watts.
Repeating Block |  | 38 | 26 | 1 | V13 | V13 |  | uint16 | % VRef | V_SF | RW | O | Point 13 Volts.
Repeating Block |  | 39 | 27 | 1 | W13 | W13 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 13 Watts.
Repeating Block |  | 40 | 28 | 1 | V14 | V14 |  | uint16 | % VRef | V_SF | RW | O | Point 14 Volts.
Repeating Block |  | 41 | 29 | 1 | W14 | W14 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 14 Watts.
Repeating Block |  | 42 | 30 | 1 | V15 | V15 |  | uint16 | % VRef | V_SF | RW | O | Point 15 Volts.
Repeating Block |  | 43 | 31 | 1 | W15 | W15 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 15 Watts.
Repeating Block |  | 44 | 32 | 1 | V16 | V16 |  | uint16 | % VRef | V_SF | RW | O | Point 16 Volts.
Repeating Block |  | 45 | 33 | 1 | W16 | W16 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 16 Watts.
Repeating Block |  | 46 | 34 | 1 | V17 | V17 |  | uint16 | % VRef | V_SF | RW | O | Point 17 Volts.
Repeating Block |  | 47 | 35 | 1 | W17 | W17 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 17 Watts.
Repeating Block |  | 48 | 36 | 1 | V18 | V18 |  | uint16 | % VRef | V_SF | RW | O | Point 18 Volts.
Repeating Block |  | 49 | 37 | 1 | W18 | W18 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 18 Watts.
Repeating Block |  | 50 | 38 | 1 | V19 | V19 |  | uint16 | % VRef | V_SF | RW | O | Point 19 Volts.
Repeating Block |  | 51 | 39 | 1 | W19 | W19 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 19 Watts.
Repeating Block |  | 52 | 40 | 1 | V20 | V20 |  | uint16 | % VRef | V_SF | RW | O | Point 20 Volts.
Repeating Block |  | 53 | 41 | 1 | W20 | W20 |  | int16 | % VRef | DeptRef_SF | RW | O | Point 20 Watts.
Repeating Block |  | 54 | 42 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 62 | 50 | 1 | RmpPt1Tms | RmpPt1Tms |  | uint16 | Secs |  | RW | O | The time of the PT1 in seconds (time to accomplish a change of 95%).
Repeating Block |  | 63 | 51 | 1 | RmpDecTmm | RmpDecTmm |  | uint16 | % WMax/min | RmpIncDec_SF | RW | O | The maximum rate at which the watt value may be reduced in response to changes in the voltage value.
Repeating Block |  | 64 | 52 | 1 | RmpIncTmm | RmpIncTmm |  | uint16 | % WMax/min | RmpIncDec_SF | RW | O | The maximum rate at which the watt value may be increased in response to changes in the voltage value.
Repeating Block |  | 65 | 53 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | DeptRef |  |  | Name: %WMax; Value: 1
enum16 | DeptRef |  |  | Name: %WAval; Value: 2
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 134
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Freq-Watt Crv | 134 | uint16 |  |  | R | M | Curve-Based Frequency-Watt | Ref 3: 8.9.1.2, 8.9.4.2
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 58) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | Is curve-based Frequency-Watt control active.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for freq-watt change.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for freq-watt curve selection.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend min. 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximum of 10).
Fixed Block |  | 9 | 7 | 1 | Hz_SF | Hz_SF |  | sunssf | SF |  | R | M | Scale factor for frequency.
Fixed Block |  | 10 | 8 | 1 | W_SF | W_SF |  | sunssf | SF |  | R | M | Scale factor for percent WRef.
Fixed Block |  | 11 | 9 | 1 | RmpIncDec_SF | RmpIncDec_SF |  | sunssf | SF |  | R | O | Scale factor for increment and decrement ramps.
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Hz1 | Hz1 |  | uint16 | Hz | Hz_SF | RW | M | Point 1 Hertz.
Repeating Block |  | 14 | 2 | 1 | W1 | W1 |  | int16 | % WRef | W_SF | RW | M | Point 1 Watts.
Repeating Block |  | 15 | 3 | 1 | Hz2 | Hz2 |  | uint16 | Hz | Hz_SF | RW | O | Point 2 Hertz.
Repeating Block |  | 16 | 4 | 1 | W2 | W2 |  | int16 | % WRef | W_SF | RW | O | Point 2 Watts.
Repeating Block |  | 17 | 5 | 1 | Hz3 | Hz3 |  | uint16 | Hz | Hz_SF | RW | O | Point 3 Hertz.
Repeating Block |  | 18 | 6 | 1 | W3 | W3 |  | int16 | % WRef | W_SF | RW | O | Point 3 Watts.
Repeating Block |  | 19 | 7 | 1 | Hz4 | Hz4 |  | uint16 | Hz | Hz_SF | RW | O | Point 4 Hertz.
Repeating Block |  | 20 | 8 | 1 | W4 | W4 |  | int16 | % WRef | W_SF | RW | O | Point 4 Watts.
Repeating Block |  | 21 | 9 | 1 | Hz5 | Hz5 |  | uint16 | Hz | Hz_SF | RW | O | Point 5 Hertz.
Repeating Block |  | 22 | 10 | 1 | W5 | W5 |  | int16 | % WRef | W_SF | RW | O | Point 5 Watts.
Repeating Block |  | 23 | 11 | 1 | Hz6 | Hz6 |  | uint16 | Hz | Hz_SF | RW | O | Point 6 Hertz.
Repeating Block |  | 24 | 12 | 1 | W6 | W6 |  | int16 | % WRef | W_SF | RW | O | Point 6 Watts.
Repeating Block |  | 25 | 13 | 1 | Hz7 | Hz7 |  | uint16 | Hz | Hz_SF | RW | O | Point 7 Hertz.
Repeating Block |  | 26 | 14 | 1 | W7 | W7 |  | int16 | % WRef | W_SF | RW | O | Point 7 Watts.
Repeating Block |  | 27 | 15 | 1 | Hz8 | Hz8 |  | uint16 | Hz | Hz_SF | RW | O | Point 8 Hertz.
Repeating Block |  | 28 | 16 | 1 | W8 | W8 |  | int16 | % WRef | W_SF | RW | O | Point 8 Watts.
Repeating Block |  | 29 | 17 | 1 | Hz9 | Hz9 |  | uint16 | Hz | Hz_SF | RW | O | Point 9 Hertz.
Repeating Block |  | 30 | 18 | 1 | W9 | W9 |  | int16 | % WRef | W_SF | RW | O | Point 9 Watts.
Repeating Block |  | 31 | 19 | 1 | Hz10 | Hz10 |  | uint16 | Hz | Hz_SF | RW | O | Point 10 Hertz.
Repeating Block |  | 32 | 20 | 1 | W10 | W10 |  | int16 | % WRef | W_SF | RW | O | Point 10 Watts.
Repeating Block |  | 33 | 21 | 1 | Hz11 | Hz11 |  | uint16 | Hz | Hz_SF | RW | O | Point 11 Hertz.
Repeating Block |  | 34 | 22 | 1 | W11 | W11 |  | int16 | % WRef | W_SF | RW | O | Point 11 Watts.
Repeating Block |  | 35 | 23 | 1 | Hz12 | Hz12 |  | uint16 | Hz | Hz_SF | RW | O | Point 12 Hertz.
Repeating Block |  | 36 | 24 | 1 | W12 | W12 |  | int16 | % WRef | W_SF | RW | O | Point 12 Watts.
Repeating Block |  | 37 | 25 | 1 | Hz13 | Hz13 |  | uint16 | Hz | Hz_SF | RW | O | Point 13 Hertz.
Repeating Block |  | 38 | 26 | 1 | W13 | W13 |  | int16 | % WRef | W_SF | RW | O | Point 13 Watts.
Repeating Block |  | 39 | 27 | 1 | Hz14 | Hz14 |  | uint16 | Hz | Hz_SF | RW | O | Point 14 Hertz.
Repeating Block |  | 40 | 28 | 1 | W14 | W14 |  | int16 | % WRef | W_SF | RW | O | Point 14 Watts.
Repeating Block |  | 41 | 29 | 1 | Hz15 | Hz15 |  | uint16 | Hz | Hz_SF | RW | O | Point 15 Hertz.
Repeating Block |  | 42 | 30 | 1 | W15 | W15 |  | int16 | % WRef | W_SF | RW | O | Point 15 Watts.
Repeating Block |  | 43 | 31 | 1 | Hz16 | Hz16 |  | uint16 | Hz | Hz_SF | RW | O | Point 16 Hertz.
Repeating Block |  | 44 | 32 | 1 | W16 | W16 |  | int16 | % WRef | W_SF | RW | O | Point 16 Watts.
Repeating Block |  | 45 | 33 | 1 | Hz17 | Hz17 |  | uint16 | Hz | Hz_SF | RW | O | Point 17 Hertz.
Repeating Block |  | 46 | 34 | 1 | W17 | W17 |  | int16 | % WRef | W_SF | RW | O | Point 17 Watts.
Repeating Block |  | 47 | 35 | 1 | Hz18 | Hz18 |  | uint16 | Hz | Hz_SF | RW | O | Point 18 Hertz.
Repeating Block |  | 48 | 36 | 1 | W18 | W18 |  | int16 | % WRef | W_SF | RW | O | Point 18 Watts.
Repeating Block |  | 49 | 37 | 1 | Hz19 | Hz19 |  | uint16 | Hz | Hz_SF | RW | O | Point 19 Hertz.
Repeating Block |  | 50 | 38 | 1 | W19 | W19 |  | int16 | % WRef | W_SF | RW | O | Point 19 Watts.
Repeating Block |  | 51 | 39 | 1 | Hz20 | Hz20 |  | uint16 | Hz | Hz_SF | RW | O | Point 20 Hertz.
Repeating Block |  | 52 | 40 | 1 | W20 | W20 |  | int16 | % WRef | W_SF | RW | O | Point 20 Watts.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve. (Max 16 chars)
Repeating Block |  | 61 | 49 | 1 | RmpPT1Tms | RmpPT1Tms |  | uint16 | Secs |  | RW | O | The time of the PT1 in seconds (time to accomplish a change of 95%).
Repeating Block |  | 62 | 50 | 1 | RmpDecTmm | RmpDecTmm |  | uint16 | % WMax/min | RmpIncDec_SF | RW | O | The maximum rate at which the power value may be reduced in response to changes in the frequency value.
Repeating Block |  | 63 | 51 | 1 | RmpIncTmm | RmpIncTmm |  | uint16 | % WMax/min | RmpIncDec_SF | RW | O | The maximum rate at which the power value may be increased in response to changes in the frequency value.
Repeating Block |  | 64 | 52 | 1 | RmpRsUp | RmpRsUp |  | uint16 | % WMax/min | RmpIncDec_SF | RW | O | The maximum rate at which the power may be increased after releasing the frozen value of snap shot function.
Repeating Block |  | 65 | 53 | 1 | SnptW | SnptW |  | bitfield16 |  |  | RW | M | 1=enable snapshot/capture mode
Repeating Block |  | 66 | 54 | 1 | WRef | WRef |  | uint16 | W | W_SF | RW | O | Reference active power (default = WMax).
Repeating Block |  | 67 | 55 | 1 | WRefStrHz | WRefStrHz |  | uint16 | Hz | Hz_SF | RW | O | Frequency deviation from nominal frequency at the time of the snapshot to start constraining power output.
Repeating Block |  | 68 | 56 | 1 | WRefStopHz | WRefStopHz |  | uint16 | Hz | Hz_SF | RW | O | Frequency deviation from nominal frequency at which to release the power output.
Repeating Block |  | 69 | 57 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 135
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | LFRT | 135 | uint16 |  |  | R | M | Low Frequency Ride-through | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 50) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | LHzRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for LFRT change. | Setting is ignored for LFRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for LFRT curve selection. | Setting is ignored for LFRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for LFRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | Hz_SF | Hz_SF |  | sunssf |  |  | R | M | Scale factor for frequency.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 1 | Tms1 | Tms1 |  | uint16 | Secs | Tms_SF | RW | M | Point 1 must disconnect duration.
Repeating Block |  | 14 | 2 | 1 | Hz1 | Hz1 |  | uint16 | Hz | Hz_SF | RW | M | Point 1 must disconnect frequency.
Repeating Block |  | 15 | 3 | 1 | Tms2 | Tms2 |  | uint16 | Secs | Tms_SF | RW | O | Point 2 must disconnect duration.
Repeating Block |  | 16 | 4 | 1 | Hz2 | Hz2 |  | uint16 | Hz | Hz_SF | RW | O | Point 2 must disconnect frequency.
Repeating Block |  | 17 | 5 | 1 | Tms3 | Tms3 |  | uint16 | Secs | Tms_SF | RW | O | Point 3 must disconnect duration.
Repeating Block |  | 18 | 6 | 1 | Hz3 | Hz3 |  | uint16 | Hz | Hz_SF | RW | O | Point 3 must disconnect frequency.
Repeating Block |  | 19 | 7 | 1 | Tms4 | Tms4 |  | uint16 | Secs | Tms_SF | RW | O | Point 4 must disconnect duration.
Repeating Block |  | 20 | 8 | 1 | Hz4 | Hz4 |  | uint16 | Hz | Hz_SF | RW | O | Point 4 must disconnect frequency.
Repeating Block |  | 21 | 9 | 1 | Tms5 | Tms5 |  | uint16 | Secs | Tms_SF | RW | O | Point 5 must disconnect duration.
Repeating Block |  | 22 | 10 | 1 | Hz5 | Hz5 |  | uint16 | Hz | Hz_SF | RW | O | Point 5 must disconnect frequency.
Repeating Block |  | 23 | 11 | 1 | Tms6 | Tms6 |  | uint16 | Secs | Tms_SF | RW | O | Point 6 must disconnect duration.
Repeating Block |  | 24 | 12 | 1 | Hz6 | Hz6 |  | uint16 | Hz | Hz_SF | RW | O | Point 6 must disconnect frequency.
Repeating Block |  | 25 | 13 | 1 | Tms7 | Tms7 |  | uint16 | Secs | Tms_SF | RW | O | Point 7 must disconnect duration.
Repeating Block |  | 26 | 14 | 1 | Hz7 | Hz7 |  | uint16 | Hz | Hz_SF | RW | O | Point 7 must disconnect frequency.
Repeating Block |  | 27 | 15 | 1 | Tms8 | Tms8 |  | uint16 | Secs | Tms_SF | RW | O | Point 8 must disconnect duration.
Repeating Block |  | 28 | 16 | 1 | Hz8 | Hz8 |  | uint16 | Hz | Hz_SF | RW | O | Point 8 must disconnect frequency.
Repeating Block |  | 29 | 17 | 1 | Tms9 | Tms9 |  | uint16 | Secs | Tms_SF | RW | O | Point 9 must disconnect duration.
Repeating Block |  | 30 | 18 | 1 | Hz9 | Hz9 |  | uint16 | Hz | Hz_SF | RW | O | Point 9 must disconnect frequency.
Repeating Block |  | 31 | 19 | 1 | Tms10 | Tms10 |  | uint16 | Secs | Tms_SF | RW | O | Point 10 must disconnect duration.
Repeating Block |  | 32 | 20 | 1 | Hz10 | Hz10 |  | uint16 | Hz | Hz_SF | RW | O | Point 10 must disconnect frequency.
Repeating Block |  | 33 | 21 | 1 | Tms11 | Tms11 |  | uint16 | Secs | Tms_SF | RW | O | Point 11 must disconnect duration.
Repeating Block |  | 34 | 22 | 1 | Hz11 | Hz11 |  | uint16 | Hz | Hz_SF | RW | O | Point 11 must disconnect frequency.
Repeating Block |  | 35 | 23 | 1 | Tms12 | Tms12 |  | uint16 | Secs | Tms_SF | RW | O | Point 12 must disconnect duration.
Repeating Block |  | 36 | 24 | 1 | Hz12 | Hz12 |  | uint16 | Hz | Hz_SF | RW | O | Point 12 must disconnect frequency.
Repeating Block |  | 37 | 25 | 1 | Tms13 | Tms13 |  | uint16 | Secs | Tms_SF | RW | O | Point 13 must disconnect duration.
Repeating Block |  | 38 | 26 | 1 | Hz13 | Hz13 |  | uint16 | Hz | Hz_SF | RW | O | Point 13 must disconnect frequency.
Repeating Block |  | 39 | 27 | 1 | Tms14 | Tms14 |  | uint16 | Secs | Tms_SF | RW | O | Point 14 must disconnect duration.
Repeating Block |  | 40 | 28 | 1 | Hz14 | Hz14 |  | uint16 | Hz | Hz_SF | RW | O | Point 14 must disconnect frequency.
Repeating Block |  | 41 | 29 | 1 | Tms15 | Tms15 |  | uint16 | Secs | Tms_SF | RW | O | Point 15 must disconnect duration.
Repeating Block |  | 42 | 30 | 1 | Hz15 | Hz15 |  | uint16 | Hz | Hz_SF | RW | O | Point 15 must disconnect frequency.
Repeating Block |  | 43 | 31 | 1 | Tms16 | Tms16 |  | uint16 | Secs | Tms_SF | RW | O | Point 16 must disconnect duration.
Repeating Block |  | 44 | 32 | 1 | Hz16 | Hz16 |  | uint16 | Hz | Hz_SF | RW | O | Point 16 must disconnect frequency.
Repeating Block |  | 45 | 33 | 1 | Tms17 | Tms17 |  | uint16 | Secs | Tms_SF | RW | O | Point 17 must disconnect duration.
Repeating Block |  | 46 | 34 | 1 | Hz17 | Hz17 |  | uint16 | Hz | Hz_SF | RW | O | Point 17 must disconnect frequency.
Repeating Block |  | 47 | 35 | 1 | Tms18 | Tms18 |  | uint16 | Secs | Tms_SF | RW | O | Point 18 must disconnect duration.
Repeating Block |  | 48 | 36 | 1 | Hz18 | Hz18 |  | uint16 | Hz | Hz_SF | RW | O | Point 18 must disconnect frequency.
Repeating Block |  | 49 | 37 | 1 | Tms19 | Tms19 |  | uint16 | Secs | Tms_SF | RW | O | Point 19 must disconnect duration.
Repeating Block |  | 50 | 38 | 1 | Hz19 | Hz19 |  | uint16 | Hz | Hz_SF | RW | O | Point 19 must disconnect frequency.
Repeating Block |  | 51 | 39 | 1 | Tms20 | Tms20 |  | uint16 | Secs | Tms_SF | RW | O | Point 20 must disconnect duration.
Repeating Block |  | 52 | 40 | 1 | Hz20 | Hz20 |  | uint16 | Hz | Hz_SF | RW | O | Point 20 must disconnect frequency.
Repeating Block |  | 53 | 41 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 61 | 49 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 145
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Extended Settings | 145 | uint16 |  |  | R | M | Inverter controls extended settings
Header |  | 1 |  | 1 | L |  | 8 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | NomRmpUpRte | Ramp Up Rate |  | uint16 | Pct | Rmp_SF | RW | O | Ramp up rate as a percentage of max current.
Fixed Block |  | 3 | 1 | 1 | NomRmpDnRte | NomRmpDnRte |  | uint16 | Pct | Rmp_SF | RW | O | Ramp down rate as a percentage of max current.
Fixed Block |  | 4 | 2 | 1 | EmgRmpUpRte | Emergency Ramp Up Rate |  | uint16 | Pct | Rmp_SF | RW | O | Emergency ramp up rate as a percentage of max current.
Fixed Block |  | 5 | 3 | 1 | EmgRmpDnRte | Emergency Ramp Down Rate |  | uint16 | Pct | Rmp_SF | RW | O | Emergency ramp down rate as a percentage of max current.
Fixed Block |  | 6 | 4 | 1 | ConnRmpUpRte | Connect Ramp Up Rate |  | uint16 | Pct | Rmp_SF | RW | O | Connect ramp up rate as a percentage of max current.
Fixed Block |  | 7 | 5 | 1 | ConnRmpDnRte | Connect Ramp Down Rate |  | uint16 | Pct | Rmp_SF | RW | O | Connect ramp down rate as a percentage of max current.
Fixed Block |  | 8 | 6 | 1 | AGra | Default Ramp Rate |  | uint16 | Pct | Rmp_SF | RW | O | Ramp rate specified in percent of max current.
Fixed Block |  | 9 | 7 | 1 | Rmp_SF | Ramp Rate Scale Factor |  | sunssf |  |  | R | O | Ramp Rate Scale Factor

## 64202
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Pika Energy Inverter Arbitrage Control | 64202 | uint16 |  |  | R | M | Power control model for Energy Island
Header |  | 1 |  | 1 | L |  | 12 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | SysMd | System Operating Mode |  | enum16 |  |  | R | M | System operating mode | must be in Sysmode 5, ARBITRAGE, for the controls in this model to take effect. It is read-only in this model. This parameter can be changed from model 64200 on the device at Modbus slave ID 1
Fixed Block |  | 3 | 1 | 1 | PMax | Max real power |  | uint16 |  | PQMax_SF | R | M | Maximum real power magnitude | applies to import and export power levels
Fixed Block |  | 4 | 2 | 1 | QMax | Max reactive power |  | uint16 |  | PQMax_SF | R | M | Maximum reactive power magnitude | applies to import and export power levels
Fixed Block |  | 5 | 3 | 1 | PMaxLimPct | Real power target |  | int16 |  | PQLimPct_SF | RW | M | target real power - -100.0% to +100.0% of PMax | take note of scale factor: -1000 to 1000 corresponds to -100.0% to 100.0%
Fixed Block |  | 6 | 4 | 1 | QMaxLimPct | Reactive power target |  | int16 |  | PQLimPct_SF | RW | M | target reactive power - -100.0% to +100.0% of QMax | take note of scale factor: -1000 to 1000 corresponds to -100.0% to 100.0%
Fixed Block |  | 7 | 5 | 1 | PQGra | Ramp rate |  | uint16 |  | PQGra_SF | RW | M | ramp rate for slewing power to target | applies to both active and reactive slewing
Fixed Block |  | 8 | 6 | 1 | PQMax_SF | PQMax_SF |  | sunssf |  |  | R | M | scale factor for max power | applies to both active and reactive power levels
Fixed Block |  | 9 | 7 | 1 | PQLimPct_SF | PQLimPct_SF |  | sunssf |  |  | R | M | scale factor for target power percentages | applies to both active and reactive power levels
Fixed Block |  | 10 | 8 | 1 | PQGra_SF | PQGra_SF |  | sunssf |  |  | R | M | scale factor for ramp rate
Fixed Block |  | 11 | 9 | 1 | CtlPr | Control priority |  | enum16 |  |  | RW | M | set control priority to real or reactive target
Fixed Block |  | 12 | 10 | 1 | PQSet_Ena | Enable arbitrage control |  | enum16 |  |  | RW | M | activate PQ control settings | must set this flag to ENABLE or UPDATE for new settings to take effect
Fixed Block |  | 13 | 11 | 1 | Conn | Connect |  | enum16 |  |  | RW | M | enable/disable inverter
enum16 | SysMd |  |  | Name: SAFETY_SHUTDOWN; Value: 0
enum16 | SysMd |  |  | Name: GRID_CONNECT; Value: 1
enum16 | SysMd |  |  | Name: SELF_SUPPLY; Value: 2
enum16 | SysMd |  |  | Name: CLEAN_BACKUP; Value: 3
enum16 | SysMd |  |  | Name: PRIORITY_BACKUP; Value: 4
enum16 | SysMd |  |  | Name: ARBITRAGE; Value: 5
enum16 | CtlPr |  |  | Name: REAL; Value: 0
enum16 | CtlPr |  |  | Name: REACTIVE; Value: 1
enum16 | PQSet_Ena |  |  | Name: DISABLE; Value: 0
enum16 | PQSet_Ena |  |  | Name: ENABLE; Value: 1
enum16 | PQSet_Ena |  |  | Name: UPDATE; Value: 2
enum16 | Conn |  |  | Name: DISCONNECT; Value: 0
enum16 | Conn |  |  | Name: CONNECT; Value: 1

## 64203
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Pika Energy Reconnect Control | 64203 | uint16 |  |  | R | M | Define grid parameters required for reconnection
Header |  | 1 |  | 1 | L |  | 12 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ModEna | ModEna |  | enum16 |  |  | RW | M | Enable this model's voltage and frequency window.
Fixed Block |  | 3 | 1 | 1 | ReConn_Tms | ReConn_Tms |  | uint16 | Secs | Tms_SF | RW | M | Time to reconnect after fault, and within frequency and voltage window.
Fixed Block |  | 4 | 2 | 1 | ReConnMinV | ReConnMinV |  | uint16 | %Vref | V_SF | RW | M | Reconnect only above this voltage
Fixed Block |  | 5 | 3 | 1 | ReConnMaxV | ReConnMaxV |  | uint16 | %Vref | V_SF | RW | M | Reconnect only below this voltage
Fixed Block |  | 6 | 4 | 1 | ReConnMinHz | ReConnMinHz |  | uint16 | Hz | Hz_SF | RW | M | Reconnect only above this frequency
Fixed Block |  | 7 | 5 | 1 | ReConnMaxHz | ReConnMaxHz |  | uint16 | Hz | Hz_SF | RW | M | Reconnect only below this frequency
Fixed Block |  | 8 | 6 | 1 | VWLatchTms | VoltWattLatchTime |  | uint16 | Secs | Tms_SF | RW | M | Delay for this amount of time after voltage is restored before reconnecting
Fixed Block |  | 9 | 7 | 1 | FWLatchTms | FreqWattLatchTime |  | uint16 | Secs | Tms_SF | RW | M | Delay for this amount of time after frequency is restored before reconnecting
Fixed Block |  | 10 | 8 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for reconnect time.
Fixed Block |  | 11 | 9 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for voltage percent of Vref.
Fixed Block |  | 12 | 10 | 1 | Hz_SF | Hz_SF |  | sunssf |  |  | R | M | Scale factor for frequency.
Fixed Block |  | 13 | 11 | Size: 1; Name: Pad; Type: pad; R/W: R | M
enum16 | ModEna |  |  | Name: DISABLE; Value: 0
enum16 | ModEna |  |  | Name: ENABLE; Value: 1

## 64204
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inverter Export | 64204 | uint16 |  |  | R | M | Grid export measurements for inverters with current transducers
Header |  | 1 |  | 1 | L |  | 8 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Px1 | Power export line 1 |  | int16 | W |  | R | M | RMS power to/from grid on line 1 | if no CTs connected, this value will be 0x8000
Fixed Block |  | 3 | 1 | 1 | Px2 | Power export line 2 |  | int16 | W |  | R | M | RMS power to/from grid on line 2 | if no CTs connected, this value will be 0x8000
Fixed Block |  | 4 | 2 | 1 | Px3 | Power export line 3 |  | int16 | W |  | R | M | RMS power to/from grid on line 3 | if no CTs connected, or if inverter is split phase, this value will be 0x8000
Fixed Block |  | 5 | 3 | 2 | Whx | Energy exported |  | acc32 | Wh |  | R | M | Energy exported to grid
Fixed Block |  | 7 | 5 | 2 | Whin | Energy imported |  | acc32 | Wh |  | R | M | Total imported energy to REbus | does not include local loads
Fixed Block |  | 9 | 7 | Size: 1; Name: Pad; Type: pad; R/W: R | M

## 64205
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Utility Compliance Configuration | 64205 | uint16 |  |  | R | M | Configure inverter settings based on utility requirements
Header |  | 1 |  | 1 | L |  | 2 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | SRD | Compliance selection |  | enum16 |  |  | RW | M | Select which utility your inverter is being installed under. | Inverter must be disabled for this selection to take effect. Different utilities require different inverter settings. This selection will define which utility settings the inverter will use. The selections will be listed with utility names and geographical locations.
Fixed Block |  | 3 | 1 | 1 | Def | Defaulted |  | enum16 |  |  | R | M | Indicates whether or not the default settings from the Compliance Selection field have been applied. | Note that this field will only update after your press submit.
enum16 | SRD |  |  | Name: IEEE_1547; Value: 0
enum16 | SRD |  |  | Name: RULE_14H_1; Value: 1
enum16 | SRD |  |  | Name: RULE_14H_2; Value: 2
enum16 | SRD |  |  | Name: RULE_21; Value: 3
enum16 | SRD |  |  | Name: RULE_PREPA; Value: 4
enum16 | Def |  |  | Name: NOT_DEFAULTED; Value: 0
enum16 | Def |  |  | Name: DEFAULTED; Value: 1

## 64206
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Energy Island Configuration | 64206 | uint16 |  |  | R | M | Configure Energy Island system settings
Header |  | 1 |  | 1 | L |  | 46 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Conn | Enable inverter |  | enum16 |  |  | RW | M | Enable inverter
Fixed Block |  | 3 | 1 | 4 | Pwd | Access code |  | uint64 |  |  | RW | M | Access code
Fixed Block |  | 7 | 5 | 1 | SRD | Compliance selection |  | pad |  |  | R | M | Select which utility your inverter is being installed under. | Inverter must be disabled for this selection to take effect. Different utilities require different inverter settings. This selection will define which utility settings the inverter will use. The selections will be listed with utility names and geographical locations.
Fixed Block |  | 8 | 6 | 1 | Def | Compliance settings defaulted |  | pad |  |  | R | M | Indicates whether or not the default settings from the Compliance Selection field have been applied. | Note that this field will only update after your press submit
Fixed Block |  | 9 | 7 | 1 | ZExp | Zero Export |  | enum16 |  |  | RW | M | When enabled, prevents the inverter from exporting power to the utility grid
Fixed Block |  | 10 | 8 | 1 | IslandEna | Enable Islanding |  | enum16 |  |  | RW | M
Fixed Block |  | 11 | 9 | 1 | ActSysMds | Enabled SysModes |  | bitfield16 |  |  | RW | M | Select the Operational Modes that will be available to this installation
Fixed Block |  | 12 | 10 | 1 | CTTrig | Trigger CT calibration |  | enum16 |  |  | RW | M | Trigger CT calibration
Fixed Block |  | 13 | 11 | 1 | ClrDisp | Clear display |  | enum16 |  |  | RW | M | Clear offline devices and reset the LCD display on the front cover of the inverter
Fixed Block |  | 14 | 12 | 1 | PLMCh | PLM channel |  | enum16 |  |  | RW | M | Power line modem channel. Default is channel 1
Fixed Block |  | 15 | 13 | 1 | PLMEna | PLM enable |  | enum16 |  |  | RW | M | Enable the inverter's power line modem. Do not disable unless guided by Pika Energy Technical Support
Fixed Block |  | 16 | 14 | 1 | GPLMRst | Global PLM Reset |  | enum16 |  |  | RW | M | Reset all online devices (including those currently on different channels) to the default PLM channel (Ch 1)
Fixed Block |  | 17 | 15 | 1 | GPLMCh | PLM Group Set |  | enum16 |  |  | RW | M | Set PLM channel for all devices (including inverter) that are currently on the inverter's channel (PLMCh) to the channel indicated by this register. This will not affect devices that aren't currently on PLMCh. PLMCh will also be set to the value of this register.
Fixed Block |  | 18 | 16 | 1 | SS_Src | Self Supply Source Power |  | uint16 | W |  | RW | M | When in Self-Supply, the CT import power level above which causes the inverter to start exporting. With sufficient battery storage and/or PV generation, this will be the maximum load the meter will see.
Fixed Block |  | 19 | 17 | 1 | SS_Sink | Self Supply Sink Power |  | uint16 | W |  | RW | M | When in Self-Supply, the CT import power level below which causes the inverter to start importing. (i.e., max rate to charge batteries from the grid)
Fixed Block |  | 20 | 18 | 1 | XFREna | Enable External Transfer |  | enum16 |  |  | RW | M | Enable the use of an external transfer switch
Fixed Block |  | 21 | 19 | Size: 1; Name: XFRV_sf; Type: sunssf; R/W: R | M
Fixed Block |  | 22 | 20 | 1 | XFRV | External Transfer Voltage |  | uint16 | V | XFRV_sf | RW | M | Grid voltage below which to transfer local loads to the inverter, and above which to transfer loads to utility mains. Default is 95.0V
Fixed Block |  | 23 | 21 | 1 | XFRTms | External Transfer timeout |  | uint16 | s |  | RW | M | Amount of time after grid voltage returns to transfer local loads back to the utility mains. Grid voltage must be above External Transer Voltage for the entire time. Default is 60 seconds
Fixed Block |  | 24 | 22 | 1 | Pad0 | Pad |  | pad |  |  | R | M | Large pad for future model expansion
Fixed Block |  | 25 | 23 | Size: 1; Name: Pad1; Type: pad; R/W: R | M
Fixed Block |  | 26 | 24 | Size: 1; Name: Pad2; Type: pad; R/W: R | M
Fixed Block |  | 27 | 25 | Size: 1; Name: Pad3; Type: pad; R/W: R | M
Fixed Block |  | 28 | 26 | Size: 1; Name: Pad4; Type: pad; R/W: R | M
Fixed Block |  | 29 | 27 | Size: 1; Name: Pad5; Type: pad; R/W: R | M
Fixed Block |  | 30 | 28 | Size: 1; Name: Pad6; Type: pad; R/W: R | M
Fixed Block |  | 31 | 29 | Size: 1; Name: Pad7; Type: pad; R/W: R | M
Fixed Block |  | 32 | 30 | Size: 1; Name: Pad8; Type: pad; R/W: R | M
Fixed Block |  | 33 | 31 | Size: 1; Name: Pad9; Type: pad; R/W: R | M
Fixed Block |  | 34 | 32 | Size: 1; Name: Pad10; Type: pad; R/W: R | M
Fixed Block |  | 35 | 33 | Size: 1; Name: Pad11; Type: pad; R/W: R | M
Fixed Block |  | 36 | 34 | Size: 1; Name: Pad12; Type: pad; R/W: R | M
Fixed Block |  | 37 | 35 | Size: 1; Name: Pad13; Type: pad; R/W: R | M
Fixed Block |  | 38 | 36 | Size: 1; Name: Pad14; Type: pad; R/W: R | M
Fixed Block |  | 39 | 37 | Size: 1; Name: Pad15; Type: pad; R/W: R | M
Fixed Block |  | 40 | 38 | Size: 1; Name: Pad16; Type: pad; R/W: R | M
Fixed Block |  | 41 | 39 | Size: 1; Name: Pad17; Type: pad; R/W: R | M
Fixed Block |  | 42 | 40 | Size: 1; Name: Pad18; Type: pad; R/W: R | M
Fixed Block |  | 43 | 41 | Size: 1; Name: Pad19; Type: pad; R/W: R | M
Fixed Block |  | 44 | 42 | Size: 1; Name: Pad20; Type: pad; R/W: R | M
Fixed Block |  | 45 | 43 | Size: 1; Name: Pad21; Type: pad; R/W: R | M
Fixed Block |  | 46 | 44 | Size: 1; Name: Pad22; Type: pad; R/W: R | M
Fixed Block |  | 47 | 45 | Size: 1; Name: Pad23; Type: pad; R/W: R | M
enum16 | Conn |  |  | Name: DISABLED; Value: 0
enum16 | Conn |  |  | Name: ENABLED; Value: 1
pad | SRD |  |  | Name: IEEE_1547; Value: 0
pad | SRD |  |  | Name: RULE_14H_1; Value: 1
pad | SRD |  |  | Name: RULE_14H_2; Value: 2
pad | SRD |  |  | Name: RULE_21; Value: 3
pad | SRD |  |  | Name: RULE_PREPA; Value: 4
pad | Def |  |  | Name: NOT_DEFAULTED; Value: 0
pad | Def |  |  | Name: DEFAULTED; Value: 1
enum16 | ZExp |  |  | Name: DISABLED; Value: 0
enum16 | ZExp |  |  | Name: ENABLED; Value: 1
enum16 | IslandEna |  |  | Name: ISLANDING_DISABLED; Value: 0
enum16 | IslandEna |  |  | Name: ISLANDING_ENABLED; Value: 1
bitfield16 | ActSysMds |  |  | Name: SAFETY_SHUTDOWN; Value: 0
bitfield16 | ActSysMds |  |  | Name: GRID_TIE; Value: 1
bitfield16 | ActSysMds |  |  | Name: SELF_SUPPLY; Value: 2
bitfield16 | ActSysMds |  |  | Name: CLEAN_BACKUP; Value: 3
bitfield16 | ActSysMds |  |  | Name: PRIORITY_BACKUP; Value: 4
bitfield16 | ActSysMds |  |  | Name: REMOTE_ARBITRAGE; Value: 5
bitfield16 | ActSysMds |  |  | Name: SELL; Value: 6
enum16 | CTTrig |  |  | Name: AUTO; Value: 0
enum16 | CTTrig |  |  | Name: TRIGGER; Value: 1
enum16 | ClrDisp |  |  | Name: NO; Value: 0
enum16 | ClrDisp |  |  | Name: CLEAR; Value: 1
enum16 | PLMCh |  |  | Name: CH_0; Value: 0
enum16 | PLMCh |  |  | Name: CH_1; Value: 1
enum16 | PLMCh |  |  | Name: CH_2; Value: 2
enum16 | PLMCh |  |  | Name: CH_3; Value: 3
enum16 | PLMCh |  |  | Name: CH_4; Value: 4
enum16 | PLMCh |  |  | Name: CH_5; Value: 5
enum16 | PLMCh |  |  | Name: CH_6; Value: 6
enum16 | PLMCh |  |  | Name: CH_7; Value: 7
enum16 | PLMCh |  |  | Name: CH_8; Value: 8
enum16 | PLMCh |  |  | Name: CH_9; Value: 9
enum16 | PLMCh |  |  | Name: CH_10; Value: 10
enum16 | PLMCh |  |  | Name: CH_11; Value: 11
enum16 | PLMCh |  |  | Name: CH_12; Value: 12
enum16 | PLMEna |  |  | Name: PLM_DISABLED; Value: 0
enum16 | PLMEna |  |  | Name: PLM_ENABLED; Value: 1
enum16 | GPLMRst |  |  | Name: RESET; Value: 1
enum16 | GPLMCh |  |  | Name: NONE; Value: 0
enum16 | GPLMCh |  |  | Name: CH_1; Value: 1
enum16 | GPLMCh |  |  | Name: CH_2; Value: 2
enum16 | GPLMCh |  |  | Name: CH_3; Value: 3
enum16 | GPLMCh |  |  | Name: CH_4; Value: 4
enum16 | GPLMCh |  |  | Name: CH_5; Value: 5
enum16 | GPLMCh |  |  | Name: CH_6; Value: 6
enum16 | GPLMCh |  |  | Name: CH_7; Value: 7
enum16 | GPLMCh |  |  | Name: CH_8; Value: 8
enum16 | GPLMCh |  |  | Name: CH_9; Value: 9
enum16 | GPLMCh |  |  | Name: CH_10; Value: 10
enum16 | GPLMCh |  |  | Name: CH_11; Value: 11
enum16 | GPLMCh |  |  | Name: CH_12; Value: 12
enum16 | XFREna |  |  | Name: DISABLED; Value: 0
enum16 | XFREna |  |  | Name: ENABLED; Value: 1

## 64207
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | REbus Status | 64207 | uint16 |  |  | R | M | REbus status data that is defined commonly across Pika Energy REbus devices
Header |  | 1 |  | 1 | L |  | 12 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | P | REbus Power |  | int16 | W |  | R | M | REbus power. Positive indicates the device is sourcing to REbus, and negative indicates sinking from REbus.
Fixed Block |  | 3 | 1 | 2 | E | Accumulated Energy |  | uint32 | Wh |  | R | M | Total accumulated energy (exact definition differs by device)
Fixed Block |  | 5 | 3 | 1 | V | REbus Voltage |  | uint16 | V | VT_sf | R | M | REbus DC Bus Voltage
Fixed Block |  | 6 | 4 | 1 | I | REbus Current |  | int16 | A | I_sf | R | M | REbus current. Positive indicates the device is sourcing to REbus, and negative indicates sinking from REbus.
Fixed Block |  | 7 | 5 | 1 | T | Device Temperature |  | int16 | Deg C | VT_sf | R | M | Device temperature
Fixed Block |  | 8 | 6 | 1 | St | State |  | enum16 |  |  | R | M |  | State is a status field used by Pika Energy for operations and maintenance purposes
Fixed Block |  | 9 | 7 | 1 | Ev | Last Event |  | enum16 |  |  | R | M |  | The most recent event that occurred on the device
Fixed Block |  | 10 | 8 | 1 | RB | REbusBits |  | bitfield16 |  |  | R | M | REbus status register
Fixed Block |  | 11 | 9 | 1 | VT_sf | VT_sf |  | sunssf |  |  | R | M | Scale factor for V and T
Fixed Block |  | 12 | 10 | 1 | I_sf | I_sf |  | sunssf |  |  | R | M | Scale factor for I
Fixed Block |  | 13 | 11 | Size: 1; Name: Pad0; Type: pad; R/W: R | M
enum16 | St |  |  | Name: UNKNOWN; Label: device offline; Value: 0
enum16 | St |  |  | Name: DISABLED; Label: disabled; Value: 16
enum16 | St |  |  | Name: INITIALIZING; Label: initializing; Value: 256
enum16 | St |  |  | Name: POWERING_UP; Label: powering up; Value: 272
enum16 | St |  |  | Name: CONNECTING_BUS; Label: connecting to REbus; Value: 288
enum16 | St |  |  | Name: DISCONNECTING_BUS; Label: disconnecting REbus; Value: 304
enum16 | St |  |  | Name: TESTING_BUS; Label: testing REbus...; Value: 320
enum16 | St |  |  | Name: LOW_BUS_VOLTAGE; Label: low REbus voltage; Value: 512
enum16 | St |  |  | Name: STANDBY; Label: standby; Value: 768
enum16 | St |  |  | Name: WAITING; Label: waiting; Value: 784
enum16 | St |  |  | Name: WAITING_NO_INPUT; Label: waiting - no input; Value: 800
enum16 | St |  |  | Name: CONNECTING_GRID; Label: connecting grid; Value: 2048
enum16 | St |  |  | Name: DISCONNECTING_GRID; Label: disconnecting grid; Value: 2064
enum16 | St |  |  | Name: GRID_CONNECTED; Label: grid connected; Value: 2080
enum16 | St |  |  | Name: ISLANDED; Label: islanded; Value: 2096
enum16 | St |  |  | Name: CONNECTING_GENERATOR; Label: connecting generator; Value: 2112
enum16 | St |  |  | Name: GENERATOR_PARALLEL; Label: generator parallel; Value: 2128
enum16 | St |  |  | Name: LOW_INPUT_VOLTAGE; Label: low input voltage; Value: 4096
enum16 | St |  |  | Name: TESTING_DEVICE_INPUT; Label: testing input...; Value: 4112
enum16 | St |  |  | Name: CONNECTING_INPUT; Label: connecting input; Value: 4352
enum16 | St |  |  | Name: DISCONNECTING_INPUT; Label: disconnecting input; Value: 4368
enum16 | St |  |  | Name: CALIBRATING; Label: calibrating; Value: 4608
enum16 | St |  |  | Name: CALIBRATION_SUCCESS; Label: calibration success!; Value: 4624
enum16 | St |  |  | Name: CALIBRATION_NEEDED; Label: calibration required; Value: 4640
enum16 | St |  |  | Name: BURN_IN; Label: burning in; Value: 4656
enum16 | St |  |  | Name: BURN_IN_DONE; Label: burn in done; Value: 4672
enum16 | St |  |  | Name: SCHEDULER_OVERRIDDEN; Label: running, overridden; Value: 4864
enum16 | St |  |  | Name: SCHEDULER_DISABLED; Label: scheduler disabled; Value: 4880
enum16 | St |  |  | Name: RUNNING; Label: running; Value: 8192
enum16 | St |  |  | Name: MAKING_POWER; Label: making power; Value: 8208
enum16 | St |  |  | Name: LIMITING_POWER; Label: limiting power; Value: 6
enum16 | St |  |  | Name: LOW_WIND; Label: low wind; Value: 12288
enum16 | St |  |  | Name: HIGH_WIND; Label: high wind; Value: 12304
enum16 | St |  |  | Name: LOW_SUN; Label: low sun; Value: 12544
enum16 | St |  |  | Name: CHARGING_BATTERY; Label: charging; Value: 24576
enum16 | St |  |  | Name: FLOAT_CHARGING_BATTERY; Label: float charging; Value: 24592
enum16 | St |  |  | Name: BULK_CHARGING_BATTERY; Label: bulk charging; Value: 24608
enum16 | St |  |  | Name: ABSORPTION_CHARGING_BATTERY; Label: absorption charging; Value: 24624
enum16 | St |  |  | Name: EQUALIZE_CHARGING_BATTERY; Label: equalizing; Value: 24640
enum16 | St |  |  | Name: DISCHARGING_BATTERY; Label: discharging; Value: 24832
enum16 | St |  |  | Name: LOW_BATTERY_VOLTAGE; Label: low battery voltage; Value: 24848
enum16 | St |  |  | Name: ERROR_GENERIC; Label: error; Value: 28672
enum16 | St |  |  | Name: OVER_VOLTAGE_INPUT; Label: over voltage input; Value: 28688
enum16 | St |  |  | Name: OVER_VOLTAGE_OUTPUT; Label: over voltage output; Value: 28704
enum16 | St |  |  | Name: OVER_CURRENT_INPUT; Label: over current input; Value: 28720
enum16 | St |  |  | Name: OVER_CURRENT_OUTPUT; Label: over current output; Value: 28736
enum16 | St |  |  | Name: ERROR_LOW_BATTERY_VOLTAGE; Label: error: low batt volts; Value: 28752
enum16 | St |  |  | Name: OVER_TEMPERATURE; Label: over temp shutdown; Value: 41216
enum16 | St |  |  | Name: GROUND_FAULT; Label: ground fault; Value: 49152
enum16 | St |  |  | Name: INSULATION_FAULT; Label: err: insulation fault; Value: 29200
enum16 | St |  |  | Name: CALIBRATION_0; Label: calibration mode; Value: 32256
enum16 | St |  |  | Name: CALIBRATION_1; Label: calibration 1; Value: 32272
enum16 | St |  |  | Name: CALIBRATION_2; Label: calibration 2; Value: 32288
enum16 | St |  |  | Name: CALIBRATION_3; Label: calibration 3; Value: 32304
enum16 | Ev |  |  | Name: GENERIC; Label: unknown event; Value: 32768
enum16 | Ev |  |  | Name: POWERUP; Label: power up; Value: 32784
enum16 | Ev |  |  | Name: SUPPLY_UNDERVOLTAGE; Label: supply under voltage; Value: 32800
enum16 | Ev |  |  | Name: DAILY_EVENT; Label: daily event; Value: 32816
enum16 | Ev |  |  | Name: ENABLE; Label: enable; Value: 33024
enum16 | Ev |  |  | Name: DISABLE; Label: disable; Value: 33280
enum16 | Ev |  |  | Name: MANUAL_DISABLE; Label: manual disable; Value: 33296
enum16 | Ev |  |  | Name: EXTERNAL_ESTOP; Label: external estop; Value: 33312
enum16 | Ev |  |  | Name: SYSMODE_CHANGE; Label: sysmode change; Value: 33536
enum16 | Ev |  |  | Name: SYSMODE_BAD; Label: unauthorized sysmode; Value: 33792
enum16 | Ev |  |  | Name: DEBUG_TRACE; Label: debug trace recorded; Value: 34048
enum16 | Ev |  |  | Name: TOU_ENTRY_ACTIVATED; Label: TOU entry activated; Value: 34304
enum16 | Ev |  |  | Name: SOFTWARE_VERSION; Label: software version; Value: 36832
enum16 | Ev |  |  | Name: HARDWARE_VERSION; Label: hardware version mismatch; Value: 36848
enum16 | Ev |  |  | Name: INTERRUPT_FAULT; Label: interrupt fault; Value: 36864
enum16 | Ev |  |  | Name: GATEDRIVE_FAULT; Label: gate drive fault; Value: 37120
enum16 | Ev |  |  | Name: TIMER_FAULT; Label: timer fault; Value: 37376
enum16 | Ev |  |  | Name: TRANSISTOR_FAILURE; Label: transistor failure; Value: 39168
enum16 | Ev |  |  | Name: OVER_TEMPERATURE; Label: over temp shutdown; Value: 41216
enum16 | Ev |  |  | Name: FAN_FAILURE; Label: fan failure; Value: 41232
enum16 | Ev |  |  | Name: FUSE_BLOWN; Label: fuse blown; Value: 41248
enum16 | Ev |  |  | Name: MISWIRING; Label: miswiring fault; Value: 41472
enum16 | Ev |  |  | Name: ALTERNATOR_BAD; Label: alternator bad; Value: 42496
enum16 | Ev |  |  | Name: REVERSE_ROTATION; Label: reverse rotation; Value: 42752
enum16 | Ev |  |  | Name: BUS_FAULT; Label: REbus fault; Value: 45056
enum16 | Ev |  |  | Name: BUS_NO_LOAD; Label: REbus no load; Value: 45072
enum16 | Ev |  |  | Name: BUS_OVER_VOLTAGE; Label: REbus over voltage; Value: 45312
enum16 | Ev |  |  | Name: BUS_UNDER_VOLTAGE; Label: REbus under voltage; Value: 45328
enum16 | Ev |  |  | Name: BUS_OVER_CURRENT; Label: REbus over current; Value: 45568
enum16 | Ev |  |  | Name: INTERNAL_OVERVOLTAGE; Label: internal over voltage; Value: 45824
enum16 | Ev |  |  | Name: BATTERY_GENERIC; Label: battery generic; Value: 47104
enum16 | Ev |  |  | Name: BATTERY_READY; Label: battery ready; Value: 47120
enum16 | Ev |  |  | Name: BATTERY_NOT_READY; Label: battery not ready; Value: 47136
enum16 | Ev |  |  | Name: BMS_GENERIC; Label: BMS generic; Value: 47360
enum16 | Ev |  |  | Name: BMS_ALARM; Label: BMS alarm; Value: 47376
enum16 | Ev |  |  | Name: BMS_WARNING; Label: BMS warning; Value: 47392
enum16 | Ev |  |  | Name: BMS_ERROR; Label: BMS error; Value: 47408
enum16 | Ev |  |  | Name: GROUND_FAULT; Label: ground fault; Value: 49152
enum16 | Ev |  |  | Name: INPUT_LOW; Label: input low; Value: 49408
enum16 | Ev |  |  | Name: INPUT_SENSOR_FAULT; Label: input sensor fault; Value: 49664
enum16 | Ev |  |  | Name: INPUT_OVER_CURRENT; Label: input over current; Value: 49920
enum16 | Ev |  |  | Name: INPUT_OVERSPEED; Label: input overspeed; Value: 50176
enum16 | Ev |  |  | Name: INPUT_HIGH; Label: input high; Value: 50432
enum16 | Ev |  |  | Name: ARC_FAULT; Label: arc fault; Value: 50688
enum16 | Ev |  |  | Name: INPUT_READY; Label: input ready; Value: 50944
enum16 | Ev |  |  | Name: GRID_FAULT; Label: grid fault; Value: 53248
enum16 | Ev |  |  | Name: GRID_OVER_VOLTAGE; Label: grid over voltage; Value: 53264
enum16 | Ev |  |  | Name: GRID_OVER_CURRENT; Label: grid over current; Value: 53280
enum16 | Ev |  |  | Name: GRID_OVER_FREQUENCY; Label: grid over frequency; Value: 53296
enum16 | Ev |  |  | Name: GRID_UNDER_VOLTAGE; Label: grid under voltage; Value: 53312
enum16 | Ev |  |  | Name: GRID_UNDER_FREQUENCY; Label: grid under frequency; Value: 53328
enum16 | Ev |  |  | Name: GRID_OVER_VOLTAGE_FAST; Label: grid overvoltage fast; Value: 53344
enum16 | Ev |  |  | Name: GRID_HIGH_IMPEDANCE; Label: grid high impedance; Value: 53360
enum16 | Ev |  |  | Name: TRANSFER_FAIL; Label: transfer sw fail; Value: 53504
enum16 | Ev |  |  | Name: SETPOINT_CRC_FAULT; Label: setpoint crc fault; Value: 57344
enum16 | Ev |  |  | Name: EEPROM_FAULT; Label: EEPROM failure; Value: 57600
enum16 | Ev |  |  | Name: FLASH_FAULT; Label: FLASH fault; Value: 57856
enum16 | Ev |  |  | Name: PLM_RESTART; Label: PLM restart; Value: 58112
enum16 | Ev |  |  | Name: DEFAULT_TRAP; Label: default trap; Value: 61440
enum16 | Ev |  |  | Name: ADDRESS_ERROR; Label: address error trap; Value: 61456
enum16 | Ev |  |  | Name: STACK_ERROR; Label: stack error trap; Value: 61472
enum16 | Ev |  |  | Name: OSCILLATOR_FAIL; Label: osc. fail trap; Value: 61488
enum16 | Ev |  |  | Name: MATH_ERROR; Label: math error trap; Value: 61504
enum16 | Ev |  |  | Name: DMAC_ERROR; Label: dmac error trap; Value: 61520
bitfield16 | RB |  |  | Name: ENABLE_MASTER; Value: 0
bitfield16 | RB |  |  | Name: ENABLE_SOURCE; Value: 1
bitfield16 | RB |  |  | Name: ENABLE_SINK; Value: 2
bitfield16 | RB |  |  | Name: REBUS_CONNECTED; Value: 3
bitfield16 | RB |  |  | Name: SOURCING; Value: 4
bitfield16 | RB |  |  | Name: SINKING; Value: 5
bitfield16 | RB |  |  | Name: LIMITING_POWER; Label: limiting power; Value: 6
bitfield16 | RB |  |  | Name: TEMP_LIMIT; Value: 7
bitfield16 | RB |  |  | Name: BUS_VOLTAGE_LOW; Value: 8
bitfield16 | RB |  |  | Name: DEV_VOLTAGE_LOW; Value: 9
bitfield16 | RB |  |  | Name: BUS_VOLTAGE_HIGH; Value: 10
bitfield16 | RB |  |  | Name: DEV_VOLTAGE_HIGH; Value: 11
bitfield16 | RB |  |  | Name: TEMPERATURE_HIGH; Value: 12
bitfield16 | RB |  |  | Name: SPT_INVALID; Value: 13
bitfield16 | RB |  |  | Name: GROUNDFAULT; Value: 14
bitfield16 | RB |  |  | Name: SUPPLY_VOLTAGE_LOW; Value: 15

## 64208
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Inverter Status | 64208 | uint16 |  |  | R | M | Miscellaneous Pika Energy inverter status registers
Header |  | 1 |  | 1 | L |  | 22 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | SysMd | System Operating Mode |  | enum16 |  |  | R | M
Fixed Block |  | 3 | 1 | 1 | CTPow | External CT Power measurement |  | int16 | W |  | R | M | Positive is exporting, negative is importing. Reads 0x8000 when CTs are not connected.
Fixed Block |  | 4 | 2 | 2 | WhIn | Total AC Energy Imported |  | uint32 | Wh |  | R | M | As measured from CTs
Fixed Block |  | 6 | 4 | 2 | WhOut | Total AC Energy Exported |  | uint32 | Wh |  | R | M | As measured from CTs
Fixed Block |  | 8 | 6 | 1 | ErrorWord | Error status |  | bitfield16 |  |  | R | M | Error status bitfield
Fixed Block |  | 9 | 7 | 1 | EnableBits | Enable bits |  | bitfield16 |  |  | R | M | Internal status register
Fixed Block |  | 10 | 8 | 1 | RelayStatus | Relay status |  | bitfield16 |  |  | R | M | Internal status register
Fixed Block |  | 11 | 9 | 1 | StatusWord | General status |  | bitfield16 |  |  | R | M | Internal status register
Fixed Block |  | 12 | 10 | 1 | LineStatus | AC Line Status |  | bitfield16 |  |  | R | M | Internal status register
Fixed Block |  | 13 | 11 | 1 | Pad0 | Pad |  | pad |  |  | R | M | Large pad for future model expansion
Fixed Block |  | 14 | 12 | Size: 1; Name: Pad1; Type: pad; R/W: R | M
Fixed Block |  | 15 | 13 | Size: 1; Name: Pad2; Type: pad; R/W: R | M
Fixed Block |  | 16 | 14 | Size: 1; Name: Pad3; Type: pad; R/W: R | M
Fixed Block |  | 17 | 15 | Size: 1; Name: Pad4; Type: pad; R/W: R | M
Fixed Block |  | 18 | 16 | Size: 1; Name: Pad5; Type: pad; R/W: R | M
Fixed Block |  | 19 | 17 | Size: 1; Name: Pad6; Type: pad; R/W: R | M
Fixed Block |  | 20 | 18 | Size: 1; Name: Pad7; Type: pad; R/W: R | M
Fixed Block |  | 21 | 19 | Size: 1; Name: Pad8; Type: pad; R/W: R | M
Fixed Block |  | 22 | 20 | Size: 1; Name: Pad9; Type: pad; R/W: R | M
Fixed Block |  | 23 | 21 | Size: 1; Name: Pad10; Type: pad; R/W: R | M
enum16 | SysMd |  |  | Name: SAFETY_SHUTDOWN; Label: Saftey Shutdown; Value: 0 |  | All devices disabled and DC bus de-energized. | Make sure to open all mechanical disconnects and test all connections with electrical meter before servicing equipment.
enum16 | SysMd |  |  | Name: GRID_TIE; Label: Grid Tie; Value: 1 |  | Support local loads and export solar power to the utility grid. | Batteries are inactive in Grid Tie mode.
enum16 | SysMd |  |  | Name: SELF_SUPPLY; Label: Self Supply; Value: 2 |  | Utilize both solar power and battery power to support local loads before exporting surplus solar to utility grid. | Battery power will not be exported to the utility grid in Self Supply. Current transformers (CTs) are required for Self Supply
enum16 | SysMd |  |  | Name: CLEAN_BACKUP; Label: Clean Backup; Value: 3 |  | Charge batteries from solar only before supporting local loads and exporting to utility grid.
enum16 | SysMd |  |  | Name: PRIORITY_BACKUP; Label: Priority Backup; Value: 4 |  | Charge batteries with both solar and the utility grid | Priority Backup will charge the batteries as fast as possible.
enum16 | SysMd |  |  | Name: REMOTE_ARBITRAGE; Value: 5
enum16 | SysMd |  |  | Name: SELL; Label: Sell; Value: 6 |  | Export full capacity, including battery power, to utility grid. | Sell mode will cause batteries to discharge to the utility grid
bitfield16 | ErrorWord |  |  | Name: LINE1_OVERCURRENT; Value: 0
bitfield16 | ErrorWord |  |  | Name: AC_PRECHARGE_FAIL; Value: 1
bitfield16 | ErrorWord |  |  | Name: DC_OVERCURRENT; Value: 2
bitfield16 | ErrorWord |  |  | Name: DC_UNBALANCED_CURRENT; Value: 3
bitfield16 | ErrorWord |  |  | Name: GATEDRIVE_FAULT; Value: 4
bitfield16 | ErrorWord |  |  | Name: BAD_THERMISTER; Value: 5
bitfield16 | ErrorWord |  |  | Name: OVERTEMP_COMP; Value: 6
bitfield16 | ErrorWord |  |  | Name: DC_PRECHARGE_FAIL; Value: 7
bitfield16 | ErrorWord |  |  | Name: XFR_SWITCH_FAIL; Value: 8
bitfield16 | ErrorWord |  |  | Name: FLASH_FAIL; Value: 9
bitfield16 | ErrorWord |  |  | Name: EEPROM_FAIL; Value: 10
bitfield16 | ErrorWord |  |  | Name: AINV_INVALID; Value: 11
bitfield16 | EnableBits |  |  | Name: DEADMAN; Value: 0
bitfield16 | EnableBits |  |  | Name: DEADMAN_UP; Value: 1
bitfield16 | EnableBits |  |  | Name: UNLOCK_GRIDSYNC; Value: 2
bitfield16 | EnableBits |  |  | Name: CTCAL; Value: 3
bitfield16 | EnableBits |  |  | Name: REBUS_CONNECT; Value: 4
bitfield16 | EnableBits |  |  | Name: GRID_DISCONNECT; Value: 5
bitfield16 | EnableBits |  |  | Name: OUTPUT_CONNECT; Value: 6
bitfield16 | EnableBits |  |  | Name: LINE3_CONNECT; Value: 7
bitfield16 | EnableBits |  |  | Name: VOLTAGE_MODE; Value: 8
bitfield16 | EnableBits |  |  | Name: CURRENT_MODE; Value: 9
bitfield16 | EnableBits |  |  | Name: BRIDGE; Value: 10
bitfield16 | EnableBits |  |  | Name: NEUT_BRIDGE; Value: 11
bitfield16 | EnableBits |  |  | Name: UNUSED12; Value: 12
bitfield16 | EnableBits |  |  | Name: AUTOFAN_ON; Value: 13
bitfield16 | EnableBits |  |  | Name: LCM_RCP; Value: 14
bitfield16 | EnableBits |  |  | Name: USB_RCP; Value: 15
bitfield16 | RelayStatus |  |  | Name: AC_PRECHARGE; Value: 0
bitfield16 | RelayStatus |  |  | Name: DC_PRECHARGE; Value: 1
bitfield16 | RelayStatus |  |  | Name: REBUS_CONNECTED; Value: 2
bitfield16 | RelayStatus |  |  | Name: REBUS_DISCONNETED; Value: 3
bitfield16 | RelayStatus |  |  | Name: GRID_CONNECTED; Value: 4
bitfield16 | RelayStatus |  |  | Name: GRID_DISCONNECTED; Value: 5
bitfield16 | RelayStatus |  |  | Name: OUTPUT_CONNECTED; Value: 6
bitfield16 | RelayStatus |  |  | Name: OUTPUT_DISCONNECTED; Value: 7
bitfield16 | RelayStatus |  |  | Name: LINE3_CONNECTED; Value: 8
bitfield16 | RelayStatus |  |  | Name: LINE3_DISCONNECTED; Value: 9
bitfield16 | RelayStatus |  |  | Name: LINE3_RETURNING; Value: 10
bitfield16 | RelayStatus |  |  | Name: UNUSED11; Value: 11
bitfield16 | RelayStatus |  |  | Name: UNUSED12; Value: 12
bitfield16 | RelayStatus |  |  | Name: UNUSED13; Value: 13
bitfield16 | RelayStatus |  |  | Name: UNUSED14; Value: 14
bitfield16 | RelayStatus |  |  | Name: UNUSED15; Value: 15
bitfield16 | StatusWord |  |  | Name: V1_LOCKED; Value: 0
bitfield16 | StatusWord |  |  | Name: V2_LOCKED; Value: 1
bitfield16 | StatusWord |  |  | Name: FREQ_LOCKED; Value: 2
bitfield16 | StatusWord |  |  | Name: PHASE_LOCKED; Value: 3
bitfield16 | StatusWord |  |  | Name: LOCKED_TO_GRID; Value: 4
bitfield16 | StatusWord |  |  | Name: PRERES_OVERTEMP; Value: 5
bitfield16 | StatusWord |  |  | Name: QPRIORITY; Value: 6
bitfield16 | StatusWord |  |  | Name: EXT_TRANSFERRED; Value: 7
bitfield16 | StatusWord |  |  | Name: MFLT_ACTIVE; Value: 8
bitfield16 | StatusWord |  |  | Name: ESTOP_ACTIVE; Value: 9
bitfield16 | StatusWord |  |  | Name: GF_ACTIVE; Value: 10
bitfield16 | StatusWord |  |  | Name: AF_ACTIVE; Value: 11
bitfield16 | StatusWord |  |  | Name: PLM_READY; Value: 12
bitfield16 | StatusWord |  |  | Name: INST_IFACE; Value: 13
bitfield16 | StatusWord |  |  | Name: XESTOP_ACTIVE; Value: 14
bitfield16 | StatusWord |  |  | Name: UNUSED15; Value: 15
bitfield16 | LineStatus |  |  | Name: V1_LOW; Value: 0
bitfield16 | LineStatus |  |  | Name: V1_HIGH; Value: 1
bitfield16 | LineStatus |  |  | Name: V2_LOW; Value: 2
bitfield16 | LineStatus |  |  | Name: V2_HIGH; Value: 3
bitfield16 | LineStatus |  |  | Name: V3_LOW; Value: 4
bitfield16 | LineStatus |  |  | Name: V3_HIGH; Value: 5
bitfield16 | LineStatus |  |  | Name: FREQ_LOW; Value: 6
bitfield16 | LineStatus |  |  | Name: FREQ_HIGH; Value: 7
bitfield16 | LineStatus |  |  | Name: UNLOCK; Value: 8
bitfield16 | LineStatus |  |  | Name: NO_ZCROSS; Value: 9
bitfield16 | LineStatus |  |  | Name: HIGH_IMP; Value: 10
bitfield16 | LineStatus |  |  | Name: GRIDFAULT; Value: 11
bitfield16 | LineStatus |  |  | Name: GT_SPLIT_OR_REVERSE; Value: 12
bitfield16 | LineStatus |  |  | Name: GT_3PHASE; Value: 13
bitfield16 | LineStatus |  |  | Name: CESSATION; Value: 14
bitfield16 | LineStatus |  |  | Name: GENMODE; Value: 15

## 64254
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | LVRTD | 64254 | uint16 |  |  | R | M | LVRT Must Disconnect | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 90) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | LVRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for LVRT change. | Setting is ignored for LVRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for LVRT curve selection. | Setting is ignored for LVRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for LVRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 2 | Tms1 | Tms1 |  | uint32 | Secs | Tms_SF | RW | M | Point 1 must disconnect duration.
Repeating Block |  | 15 | 3 | 1 | V1 | V1 |  | uint16 | V | V_SF | RW | M | Point 1 must disconnect voltage.
Repeating Block |  | 16 | 4 | 1 | Fn1 | Fn1 |  | enum16 |  |  | RW | M | Point 1 special behavior.
Repeating Block |  | 17 | 5 | 2 | Tms2 | Tms2 |  | uint32 | Secs | Tms_SF | RW | O | Point 2 must disconnect duration.
Repeating Block |  | 19 | 7 | 1 | V2 | V2 |  | uint16 | V | V_SF | RW | O | Point 2 must disconnect voltage.
Repeating Block |  | 20 | 8 | 1 | Fn2 | Fn2 |  | enum16 |  |  | RW | O | Point 2 special behavior.
Repeating Block |  | 21 | 9 | 2 | Tms3 | Tms3 |  | uint32 | Secs | Tms_SF | RW | O | Point 3 must disconnect duration.
Repeating Block |  | 23 | 11 | 1 | V3 | V3 |  | uint16 | V | V_SF | RW | O | Point 3 must disconnect voltage.
Repeating Block |  | 24 | 12 | 1 | Fn3 | Fn3 |  | enum16 |  |  | RW | O | Point 3 special behavior.
Repeating Block |  | 25 | 13 | 2 | Tms4 | Tms4 |  | uint32 | Secs | Tms_SF | RW | O | Point 4 must disconnect duration.
Repeating Block |  | 27 | 15 | 1 | V4 | V4 |  | uint16 | V | V_SF | RW | O | Point 4 must disconnect voltage.
Repeating Block |  | 28 | 16 | 1 | Fn4 | Fn4 |  | enum16 |  |  | RW | O | Point 4 special behavior.
Repeating Block |  | 29 | 17 | 2 | Tms5 | Tms5 |  | uint32 | Secs | Tms_SF | RW | O | Point 5 must disconnect duration.
Repeating Block |  | 31 | 19 | 1 | V5 | V5 |  | uint16 | V | V_SF | RW | O | Point 5 must disconnect voltage.
Repeating Block |  | 32 | 20 | 1 | Fn5 | Fn5 |  | enum16 |  |  | RW | O | Point 5 special behavior.
Repeating Block |  | 33 | 21 | 2 | Tms6 | Tms6 |  | uint32 | Secs | Tms_SF | RW | O | Point 6 must disconnect duration.
Repeating Block |  | 35 | 23 | 1 | V6 | V6 |  | uint16 | V | V_SF | RW | O | Point 6 must disconnect voltage.
Repeating Block |  | 36 | 24 | 1 | Fn6 | Fn6 |  | enum16 |  |  | RW | O | Point 6 special behavior.
Repeating Block |  | 37 | 25 | 2 | Tms7 | Tms7 |  | uint32 | Secs | Tms_SF | RW | O | Point 7 must disconnect duration.
Repeating Block |  | 39 | 27 | 1 | V7 | V7 |  | uint16 | V | V_SF | RW | O | Point 7 must disconnect voltage.
Repeating Block |  | 40 | 28 | 1 | Fn7 | Fn7 |  | enum16 |  |  | RW | O | Point 7 special behavior.
Repeating Block |  | 41 | 29 | 2 | Tms8 | Tms8 |  | uint32 | Secs | Tms_SF | RW | O | Point 8 must disconnect duration.
Repeating Block |  | 43 | 31 | 1 | V8 | V8 |  | uint16 | V | V_SF | RW | O | Point 8 must disconnect voltage.
Repeating Block |  | 44 | 32 | 1 | Fn8 | Fn8 |  | enum16 |  |  | RW | O | Point 8 special behavior.
Repeating Block |  | 45 | 33 | 2 | Tms9 | Tms9 |  | uint32 | Secs | Tms_SF | RW | O | Point 9 must disconnect duration.
Repeating Block |  | 47 | 35 | 1 | V9 | V9 |  | uint16 | V | V_SF | RW | O | Point 9 must disconnect voltage.
Repeating Block |  | 48 | 36 | 1 | Fn9 | Fn9 |  | enum16 |  |  | RW | O | Point 9 special behavior.
Repeating Block |  | 49 | 37 | 2 | Tms10 | Tms10 |  | uint32 | Secs | Tms_SF | RW | O | Point 10 must disconnect duration.
Repeating Block |  | 51 | 39 | 1 | V10 | V10 |  | uint16 | V | V_SF | RW | O | Point 10 must disconnect voltage.
Repeating Block |  | 52 | 40 | 1 | Fn10 | Fn10 |  | enum16 |  |  | RW | O | Point 10 special behavior.
Repeating Block |  | 53 | 41 | 2 | Tms11 | Tms11 |  | uint32 | Secs | Tms_SF | RW | O | Point 11 must disconnect duration.
Repeating Block |  | 55 | 43 | 1 | V11 | V11 |  | uint16 | V | V_SF | RW | O | Point 11 must disconnect voltage.
Repeating Block |  | 56 | 44 | 1 | Fn11 | Fn11 |  | enum16 |  |  | RW | O | Point 11 special behavior.
Repeating Block |  | 57 | 45 | 2 | Tms12 | Tms12 |  | uint32 | Secs | Tms_SF | RW | O | Point 12 must disconnect duration.
Repeating Block |  | 59 | 47 | 1 | V12 | V12 |  | uint16 | V | V_SF | RW | O | Point 12 must disconnect voltage.
Repeating Block |  | 60 | 48 | 1 | Fn12 | Fn12 |  | enum16 |  |  | RW | O | Point 12 special behavior.
Repeating Block |  | 61 | 49 | 2 | Tms13 | Tms13 |  | uint32 | Secs | Tms_SF | RW | O | Point 13 must disconnect duration.
Repeating Block |  | 63 | 51 | 1 | V13 | V13 |  | uint16 | V | V_SF | RW | O | Point 13 must disconnect voltage.
Repeating Block |  | 64 | 52 | 1 | Fn13 | Fn13 |  | enum16 |  |  | RW | O | Point 13 special behavior.
Repeating Block |  | 65 | 53 | 2 | Tms14 | Tms14 |  | uint32 | Secs | Tms_SF | RW | O | Point 14 must disconnect duration.
Repeating Block |  | 67 | 55 | 1 | V14 | V14 |  | uint16 | V | V_SF | RW | O | Point 14 must disconnect voltage.
Repeating Block |  | 68 | 56 | 1 | Fn14 | Fn14 |  | enum16 |  |  | RW | O | Point 14 special behavior.
Repeating Block |  | 69 | 57 | 2 | Tms15 | Tms15 |  | uint32 | Secs | Tms_SF | RW | O | Point 15 must disconnect duration.
Repeating Block |  | 71 | 59 | 1 | V15 | V15 |  | uint16 | V | V_SF | RW | O | Point 15 must disconnect voltage.
Repeating Block |  | 72 | 60 | 1 | Fn15 | Fn15 |  | enum16 |  |  | RW | O | Point 15 special behavior.
Repeating Block |  | 73 | 61 | 2 | Tms16 | Tms16 |  | uint32 | Secs | Tms_SF | RW | O | Point 16 must disconnect duration.
Repeating Block |  | 75 | 63 | 1 | V16 | V16 |  | uint16 | V | V_SF | RW | O | Point 16 must disconnect voltage.
Repeating Block |  | 76 | 64 | 1 | Fn16 | Fn16 |  | enum16 |  |  | RW | O | Point 16 special behavior.
Repeating Block |  | 77 | 65 | 2 | Tms17 | Tms17 |  | uint32 | Secs | Tms_SF | RW | O | Point 17 must disconnect duration.
Repeating Block |  | 79 | 67 | 1 | V17 | V17 |  | uint16 | V | V_SF | RW | O | Point 17 must disconnect voltage.
Repeating Block |  | 80 | 68 | 1 | Fn17 | Fn17 |  | enum16 |  |  | RW | O | Point 17 special behavior.
Repeating Block |  | 81 | 69 | 2 | Tms18 | Tms18 |  | uint32 | Secs | Tms_SF | RW | O | Point 18 must disconnect duration.
Repeating Block |  | 83 | 71 | 1 | V18 | V18 |  | uint16 | V | V_SF | RW | O | Point 18 must disconnect voltage.
Repeating Block |  | 84 | 72 | 1 | Fn18 | Fn18 |  | enum16 |  |  | RW | O | Point 18 special behavior.
Repeating Block |  | 85 | 73 | 2 | Tms19 | Tms19 |  | uint32 | Secs | Tms_SF | RW | O | Point 19 must disconnect duration.
Repeating Block |  | 87 | 75 | 1 | V19 | V19 |  | uint16 | V | V_SF | RW | O | Point 19 must disconnect voltage.
Repeating Block |  | 88 | 76 | 1 | Fn19 | Fn19 |  | enum16 |  |  | RW | O | Point 19 special behavior.
Repeating Block |  | 89 | 77 | 2 | Tms20 | Tms20 |  | uint32 | Secs | Tms_SF | RW | O | Point 20 must disconnect duration.
Repeating Block |  | 91 | 79 | 1 | V20 | V20 |  | uint16 | V | V_SF | RW | O | Point 20 must disconnect voltage.
Repeating Block |  | 92 | 80 | 1 | Fn20 | Fn20 |  | enum16 |  |  | RW | O | Point 20 special behavior.
Repeating Block |  | 93 | 81 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 101 | 89 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | Fn1 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn2 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn3 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn4 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn5 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn6 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn7 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn8 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn9 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn10 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn11 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn12 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn13 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn14 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn15 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn16 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn17 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn18 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn19 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn20 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 64255
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | HVRTD | 64255 | uint16 |  |  | R | M | HVRT Must Disconnect | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 90) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | HVRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for HVRT change. | Setting is ignored for HVRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for HVRT curve selection. | Setting is ignored for HVRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for HVRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for percent VRef.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 2 | Tms1 | Tms1 |  | uint32 | Secs | Tms_SF | RW | M | Point 1 must disconnect duration.
Repeating Block |  | 15 | 3 | 1 | V1 | V1 |  | uint16 | V | V_SF | RW | M | Point 1 must disconnect voltage.
Repeating Block |  | 16 | 4 | 1 | Fn1 | Fn1 |  | enum16 |  |  | RW | M | Point 1 special behavior.
Repeating Block |  | 17 | 5 | 2 | Tms2 | Tms2 |  | uint32 | Secs | Tms_SF | RW | O | Point 2 must disconnect duration.
Repeating Block |  | 19 | 7 | 1 | V2 | V2 |  | uint16 | V | V_SF | RW | O | Point 2 must disconnect voltage.
Repeating Block |  | 20 | 8 | 1 | Fn2 | Fn2 |  | enum16 |  |  | RW | O | Point 2 special behavior.
Repeating Block |  | 21 | 9 | 2 | Tms3 | Tms3 |  | uint32 | Secs | Tms_SF | RW | O | Point 3 must disconnect duration.
Repeating Block |  | 23 | 11 | 1 | V3 | V3 |  | uint16 | V | V_SF | RW | O | Point 3 must disconnect voltage.
Repeating Block |  | 24 | 12 | 1 | Fn3 | Fn3 |  | enum16 |  |  | RW | O | Point 3 special behavior.
Repeating Block |  | 25 | 13 | 2 | Tms4 | Tms4 |  | uint32 | Secs | Tms_SF | RW | O | Point 4 must disconnect duration.
Repeating Block |  | 27 | 15 | 1 | V4 | V4 |  | uint16 | V | V_SF | RW | O | Point 4 must disconnect voltage.
Repeating Block |  | 28 | 16 | 1 | Fn4 | Fn4 |  | enum16 |  |  | RW | O | Point 4 special behavior.
Repeating Block |  | 29 | 17 | 2 | Tms5 | Tms5 |  | uint32 | Secs | Tms_SF | RW | O | Point 5 must disconnect duration.
Repeating Block |  | 31 | 19 | 1 | V5 | V5 |  | uint16 | V | V_SF | RW | O | Point 5 must disconnect voltage.
Repeating Block |  | 32 | 20 | 1 | Fn5 | Fn5 |  | enum16 |  |  | RW | O | Point 5 special behavior.
Repeating Block |  | 33 | 21 | 2 | Tms6 | Tms6 |  | uint32 | Secs | Tms_SF | RW | O | Point 6 must disconnect duration.
Repeating Block |  | 35 | 23 | 1 | V6 | V6 |  | uint16 | V | V_SF | RW | O | Point 6 must disconnect voltage.
Repeating Block |  | 36 | 24 | 1 | Fn6 | Fn6 |  | enum16 |  |  | RW | O | Point 6 special behavior.
Repeating Block |  | 37 | 25 | 2 | Tms7 | Tms7 |  | uint32 | Secs | Tms_SF | RW | O | Point 7 must disconnect duration.
Repeating Block |  | 39 | 27 | 1 | V7 | V7 |  | uint16 | V | V_SF | RW | O | Point 7 must disconnect voltage.
Repeating Block |  | 40 | 28 | 1 | Fn7 | Fn7 |  | enum16 |  |  | RW | O | Point 7 special behavior.
Repeating Block |  | 41 | 29 | 2 | Tms8 | Tms8 |  | uint32 | Secs | Tms_SF | RW | O | Point 8 must disconnect duration.
Repeating Block |  | 43 | 31 | 1 | V8 | V8 |  | uint16 | V | V_SF | RW | O | Point 8 must disconnect voltage.
Repeating Block |  | 44 | 32 | 1 | Fn8 | Fn8 |  | enum16 |  |  | RW | O | Point 8 special behavior.
Repeating Block |  | 45 | 33 | 2 | Tms9 | Tms9 |  | uint32 | Secs | Tms_SF | RW | O | Point 9 must disconnect duration.
Repeating Block |  | 47 | 35 | 1 | V9 | V9 |  | uint16 | V | V_SF | RW | O | Point 9 must disconnect voltage.
Repeating Block |  | 48 | 36 | 1 | Fn9 | Fn9 |  | enum16 |  |  | RW | O | Point 9 special behavior.
Repeating Block |  | 49 | 37 | 2 | Tms10 | Tms10 |  | uint32 | Secs | Tms_SF | RW | O | Point 10 must disconnect duration.
Repeating Block |  | 51 | 39 | 1 | V10 | V10 |  | uint16 | V | V_SF | RW | O | Point 10 must disconnect voltage.
Repeating Block |  | 52 | 40 | 1 | Fn10 | Fn10 |  | enum16 |  |  | RW | O | Point 10 special behavior.
Repeating Block |  | 53 | 41 | 2 | Tms11 | Tms11 |  | uint32 | Secs | Tms_SF | RW | O | Point 11 must disconnect duration.
Repeating Block |  | 55 | 43 | 1 | V11 | V11 |  | uint16 | V | V_SF | RW | O | Point 11 must disconnect voltage.
Repeating Block |  | 56 | 44 | 1 | Fn11 | Fn11 |  | enum16 |  |  | RW | O | Point 11 special behavior.
Repeating Block |  | 57 | 45 | 2 | Tms12 | Tms12 |  | uint32 | Secs | Tms_SF | RW | O | Point 12 must disconnect duration.
Repeating Block |  | 59 | 47 | 1 | V12 | V12 |  | uint16 | V | V_SF | RW | O | Point 12 must disconnect voltage.
Repeating Block |  | 60 | 48 | 1 | Fn12 | Fn12 |  | enum16 |  |  | RW | O | Point 12 special behavior.
Repeating Block |  | 61 | 49 | 2 | Tms13 | Tms13 |  | uint32 | Secs | Tms_SF | RW | O | Point 13 must disconnect duration.
Repeating Block |  | 63 | 51 | 1 | V13 | V13 |  | uint16 | V | V_SF | RW | O | Point 13 must disconnect voltage.
Repeating Block |  | 64 | 52 | 1 | Fn13 | Fn13 |  | enum16 |  |  | RW | O | Point 13 special behavior.
Repeating Block |  | 65 | 53 | 2 | Tms14 | Tms14 |  | uint32 | Secs | Tms_SF | RW | O | Point 14 must disconnect duration.
Repeating Block |  | 67 | 55 | 1 | V14 | V14 |  | uint16 | V | V_SF | RW | O | Point 14 must disconnect voltage.
Repeating Block |  | 68 | 56 | 1 | Fn14 | Fn14 |  | enum16 |  |  | RW | O | Point 14 special behavior.
Repeating Block |  | 69 | 57 | 2 | Tms15 | Tms15 |  | uint32 | Secs | Tms_SF | RW | O | Point 15 must disconnect duration.
Repeating Block |  | 71 | 59 | 1 | V15 | V15 |  | uint16 | V | V_SF | RW | O | Point 15 must disconnect voltage.
Repeating Block |  | 72 | 60 | 1 | Fn15 | Fn15 |  | enum16 |  |  | RW | O | Point 15 special behavior.
Repeating Block |  | 73 | 61 | 2 | Tms16 | Tms16 |  | uint32 | Secs | Tms_SF | RW | O | Point 16 must disconnect duration.
Repeating Block |  | 75 | 63 | 1 | V16 | V16 |  | uint16 | V | V_SF | RW | O | Point 16 must disconnect voltage.
Repeating Block |  | 76 | 64 | 1 | Fn16 | Fn16 |  | enum16 |  |  | RW | O | Point 16 special behavior.
Repeating Block |  | 77 | 65 | 2 | Tms17 | Tms17 |  | uint32 | Secs | Tms_SF | RW | O | Point 17 must disconnect duration.
Repeating Block |  | 79 | 67 | 1 | V17 | V17 |  | uint16 | V | V_SF | RW | O | Point 17 must disconnect voltage.
Repeating Block |  | 80 | 68 | 1 | Fn17 | Fn17 |  | enum16 |  |  | RW | O | Point 17 special behavior.
Repeating Block |  | 81 | 69 | 2 | Tms18 | Tms18 |  | uint32 | Secs | Tms_SF | RW | O | Point 18 must disconnect duration.
Repeating Block |  | 83 | 71 | 1 | V18 | V18 |  | uint16 | V | V_SF | RW | O | Point 18 must disconnect voltage.
Repeating Block |  | 84 | 72 | 1 | Fn18 | Fn18 |  | enum16 |  |  | RW | O | Point 18 special behavior.
Repeating Block |  | 85 | 73 | 2 | Tms19 | Tms19 |  | uint32 | Secs | Tms_SF | RW | O | Point 19 must disconnect duration.
Repeating Block |  | 87 | 75 | 1 | V19 | V19 |  | uint16 | V | V_SF | RW | O | Point 19 must disconnect voltage.
Repeating Block |  | 88 | 76 | 1 | Fn19 | Fn19 |  | enum16 |  |  | RW | O | Point 19 special behavior.
Repeating Block |  | 89 | 77 | 2 | Tms20 | Tms20 |  | uint32 | Secs | Tms_SF | RW | O | Point 20 must disconnect duration.
Repeating Block |  | 91 | 79 | 1 | V20 | V20 |  | uint16 | V | V_SF | RW | O | Point 20 must disconnect voltage.
Repeating Block |  | 92 | 80 | 1 | Fn20 | Fn20 |  | enum16 |  |  | RW | O | Point 20 special behavior.
Repeating Block |  | 93 | 81 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 101 | 89 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | Fn1 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn2 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn3 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn4 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn5 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn6 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn7 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn8 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn9 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn10 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn11 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn12 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn13 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn14 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn15 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn16 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn17 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn18 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn19 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn20 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 64256
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | LFRT | 64256 | uint16 |  |  | R | M | Low Frequency Ride-through | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 90) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | LHzRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for LFRT change. | Setting is ignored for LFRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for LFRT curve selection. | Setting is ignored for LFRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for LFRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | Hz_SF | Hz_SF |  | sunssf |  |  | R | M | Scale factor for frequency.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 2 | Tms1 | Tms1 |  | uint32 | Secs | Tms_SF | RW | M | Point 1 must disconnect duration.
Repeating Block |  | 15 | 3 | 1 | Hz1 | Hz1 |  | uint16 | Hz | Hz_SF | RW | M | Point 1 must disconnect frequency.
Repeating Block |  | 16 | 4 | 1 | Fn1 | Fn1 |  | enum16 |  |  | RW | M | Point 1 special behavior.
Repeating Block |  | 17 | 5 | 2 | Tms2 | Tms2 |  | uint32 | Secs | Tms_SF | RW | O | Point 2 must disconnect duration.
Repeating Block |  | 19 | 7 | 1 | Hz2 | Hz2 |  | uint16 | Hz | Hz_SF | RW | O | Point 2 must disconnect frequency.
Repeating Block |  | 20 | 8 | 1 | Fn2 | Fn2 |  | enum16 |  |  | RW | O | Point 2 special behavior.
Repeating Block |  | 21 | 9 | 2 | Tms3 | Tms3 |  | uint32 | Secs | Tms_SF | RW | O | Point 3 must disconnect duration.
Repeating Block |  | 23 | 11 | 1 | Hz3 | Hz3 |  | uint16 | Hz | Hz_SF | RW | O | Point 3 must disconnect frequency.
Repeating Block |  | 24 | 12 | 1 | Fn3 | Fn3 |  | enum16 |  |  | RW | O | Point 3 special behavior.
Repeating Block |  | 25 | 13 | 2 | Tms4 | Tms4 |  | uint32 | Secs | Tms_SF | RW | O | Point 4 must disconnect duration.
Repeating Block |  | 27 | 15 | 1 | Hz4 | Hz4 |  | uint16 | Hz | Hz_SF | RW | O | Point 4 must disconnect frequency.
Repeating Block |  | 28 | 16 | 1 | Fn4 | Fn4 |  | enum16 |  |  | RW | O | Point 4 special behavior.
Repeating Block |  | 29 | 17 | 2 | Tms5 | Tms5 |  | uint32 | Secs | Tms_SF | RW | O | Point 5 must disconnect duration.
Repeating Block |  | 31 | 19 | 1 | Hz5 | Hz5 |  | uint16 | Hz | Hz_SF | RW | O | Point 5 must disconnect frequency.
Repeating Block |  | 32 | 20 | 1 | Fn5 | Fn5 |  | enum16 |  |  | RW | O | Point 5 special behavior.
Repeating Block |  | 33 | 21 | 2 | Tms6 | Tms6 |  | uint32 | Secs | Tms_SF | RW | O | Point 6 must disconnect duration.
Repeating Block |  | 35 | 23 | 1 | Hz6 | Hz6 |  | uint16 | Hz | Hz_SF | RW | O | Point 6 must disconnect frequency.
Repeating Block |  | 36 | 24 | 1 | Fn6 | Fn6 |  | enum16 |  |  | RW | O | Point 6 special behavior.
Repeating Block |  | 37 | 25 | 2 | Tms7 | Tms7 |  | uint32 | Secs | Tms_SF | RW | O | Point 7 must disconnect duration.
Repeating Block |  | 39 | 27 | 1 | Hz7 | Hz7 |  | uint16 | Hz | Hz_SF | RW | O | Point 7 must disconnect frequency.
Repeating Block |  | 40 | 28 | 1 | Fn7 | Fn7 |  | enum16 |  |  | RW | O | Point 7 special behavior.
Repeating Block |  | 41 | 29 | 2 | Tms8 | Tms8 |  | uint32 | Secs | Tms_SF | RW | O | Point 8 must disconnect duration.
Repeating Block |  | 43 | 31 | 1 | Hz8 | Hz8 |  | uint16 | Hz | Hz_SF | RW | O | Point 8 must disconnect frequency.
Repeating Block |  | 44 | 32 | 1 | Fn8 | Fn8 |  | enum16 |  |  | RW | O | Point 8 special behavior.
Repeating Block |  | 45 | 33 | 2 | Tms9 | Tms9 |  | uint32 | Secs | Tms_SF | RW | O | Point 9 must disconnect duration.
Repeating Block |  | 47 | 35 | 1 | Hz9 | Hz9 |  | uint16 | Hz | Hz_SF | RW | O | Point 9 must disconnect frequency.
Repeating Block |  | 48 | 36 | 1 | Fn9 | Fn9 |  | enum16 |  |  | RW | O | Point 9 special behavior.
Repeating Block |  | 49 | 37 | 2 | Tms10 | Tms10 |  | uint32 | Secs | Tms_SF | RW | O | Point 10 must disconnect duration.
Repeating Block |  | 51 | 39 | 1 | Hz10 | Hz10 |  | uint16 | Hz | Hz_SF | RW | O | Point 10 must disconnect frequency.
Repeating Block |  | 52 | 40 | 1 | Fn10 | Fn10 |  | enum16 |  |  | RW | O | Point 10 special behavior.
Repeating Block |  | 53 | 41 | 2 | Tms11 | Tms11 |  | uint32 | Secs | Tms_SF | RW | O | Point 11 must disconnect duration.
Repeating Block |  | 55 | 43 | 1 | Hz11 | Hz11 |  | uint16 | Hz | Hz_SF | RW | O | Point 11 must disconnect frequency.
Repeating Block |  | 56 | 44 | 1 | Fn11 | Fn11 |  | enum16 |  |  | RW | O | Point 11 special behavior.
Repeating Block |  | 57 | 45 | 2 | Tms12 | Tms12 |  | uint32 | Secs | Tms_SF | RW | O | Point 12 must disconnect duration.
Repeating Block |  | 59 | 47 | 1 | Hz12 | Hz12 |  | uint16 | Hz | Hz_SF | RW | O | Point 12 must disconnect frequency.
Repeating Block |  | 60 | 48 | 1 | Fn12 | Fn12 |  | enum16 |  |  | RW | O | Point 12 special behavior.
Repeating Block |  | 61 | 49 | 2 | Tms13 | Tms13 |  | uint32 | Secs | Tms_SF | RW | O | Point 13 must disconnect duration.
Repeating Block |  | 63 | 51 | 1 | Hz13 | Hz13 |  | uint16 | Hz | Hz_SF | RW | O | Point 13 must disconnect frequency.
Repeating Block |  | 64 | 52 | 1 | Fn13 | Fn13 |  | enum16 |  |  | RW | O | Point 13 special behavior.
Repeating Block |  | 65 | 53 | 2 | Tms14 | Tms14 |  | uint32 | Secs | Tms_SF | RW | O | Point 14 must disconnect duration.
Repeating Block |  | 67 | 55 | 1 | Hz14 | Hz14 |  | uint16 | Hz | Hz_SF | RW | O | Point 14 must disconnect frequency.
Repeating Block |  | 68 | 56 | 1 | Fn14 | Fn14 |  | enum16 |  |  | RW | O | Point 14 special behavior.
Repeating Block |  | 69 | 57 | 2 | Tms15 | Tms15 |  | uint32 | Secs | Tms_SF | RW | O | Point 15 must disconnect duration.
Repeating Block |  | 71 | 59 | 1 | Hz15 | Hz15 |  | uint16 | Hz | Hz_SF | RW | O | Point 15 must disconnect frequency.
Repeating Block |  | 72 | 60 | 1 | Fn15 | Fn15 |  | enum16 |  |  | RW | O | Point 15 special behavior.
Repeating Block |  | 73 | 61 | 2 | Tms16 | Tms16 |  | uint32 | Secs | Tms_SF | RW | O | Point 16 must disconnect duration.
Repeating Block |  | 75 | 63 | 1 | Hz16 | Hz16 |  | uint16 | Hz | Hz_SF | RW | O | Point 16 must disconnect frequency.
Repeating Block |  | 76 | 64 | 1 | Fn16 | Fn16 |  | enum16 |  |  | RW | O | Point 16 special behavior.
Repeating Block |  | 77 | 65 | 2 | Tms17 | Tms17 |  | uint32 | Secs | Tms_SF | RW | O | Point 17 must disconnect duration.
Repeating Block |  | 79 | 67 | 1 | Hz17 | Hz17 |  | uint16 | Hz | Hz_SF | RW | O | Point 17 must disconnect frequency.
Repeating Block |  | 80 | 68 | 1 | Fn17 | Fn17 |  | enum16 |  |  | RW | O | Point 17 special behavior.
Repeating Block |  | 81 | 69 | 2 | Tms18 | Tms18 |  | uint32 | Secs | Tms_SF | RW | O | Point 18 must disconnect duration.
Repeating Block |  | 83 | 71 | 1 | Hz18 | Hz18 |  | uint16 | Hz | Hz_SF | RW | O | Point 18 must disconnect frequency.
Repeating Block |  | 84 | 72 | 1 | Fn18 | Fn18 |  | enum16 |  |  | RW | O | Point 18 special behavior.
Repeating Block |  | 85 | 73 | 2 | Tms19 | Tms19 |  | uint32 | Secs | Tms_SF | RW | O | Point 19 must disconnect duration.
Repeating Block |  | 87 | 75 | 1 | Hz19 | Hz19 |  | uint16 | Hz | Hz_SF | RW | O | Point 19 must disconnect frequency.
Repeating Block |  | 88 | 76 | 1 | Fn19 | Fn19 |  | enum16 |  |  | RW | O | Point 19 special behavior.
Repeating Block |  | 89 | 77 | 2 | Tms20 | Tms20 |  | uint32 | Secs | Tms_SF | RW | O | Point 20 must disconnect duration.
Repeating Block |  | 91 | 79 | 1 | Hz20 | Hz20 |  | uint16 | Hz | Hz_SF | RW | O | Point 20 must disconnect frequency.
Repeating Block |  | 92 | 80 | 1 | Fn20 | Fn20 |  | enum16 |  |  | RW | O | Point 20 special behavior.
Repeating Block |  | 93 | 81 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 101 | 89 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | Fn1 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn2 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn3 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn4 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn5 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn6 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn7 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn8 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn9 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn10 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn11 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn12 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn13 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn14 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn15 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn16 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn17 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn18 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn19 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn20 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1

## 64257
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | HFRT | 64257 | uint16 |  |  | R | M | High Frequency Ride-through | Ref 4: 11
Header |  | 1 |  | 1 | L |  | 10 + (RB Count * 90) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ActCrv | ActCrv |  | uint16 |  |  | RW | M | Index of active curve. 0=no active curve.
Fixed Block |  | 3 | 1 | 1 | ModEna | ModEna |  | bitfield16 |  |  | RW | M | HFRT control mode. Enable active curve. Bitfield value.
Fixed Block |  | 4 | 2 | 1 | WinTms | WinTms |  | uint16 | Secs |  | RW | O | Time window for HFRT change. | Setting is ignored for HFRT controls.
Fixed Block |  | 5 | 3 | 1 | RvrtTms | RvrtTms |  | uint16 | Secs |  | RW | O | Timeout period for HFRT curve selection. | Setting is ignored for HFRT controls.
Fixed Block |  | 6 | 4 | 1 | RmpTms | RmpTms |  | uint16 | Secs |  | RW | O | Ramp time for moving from current mode to new mode. | Setting is ignored for HFRT controls.
Fixed Block |  | 7 | 5 | 1 | NCrv | NCrv |  | uint16 |  |  | R | M | Number of curves supported (recommend 4).
Fixed Block |  | 8 | 6 | 1 | NPt | NPt |  | uint16 |  |  | R | M | Number of curve points supported (maximumn of 20).
Fixed Block |  | 9 | 7 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for duration.
Fixed Block |  | 10 | 8 | 1 | Hz_SF | Hz_SF |  | sunssf |  |  | R | M | Scale factor for frequency.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | O
Repeating Block |  | 12 | 0 | 1 | ActPt | ActPt |  | uint16 |  |  | RW | M | Number of active points in array.
Repeating Block |  | 13 | 1 | 2 | Tms1 | Tms1 |  | uint32 | Secs | Tms_SF | RW | M | Point 1 must disconnect duration.
Repeating Block |  | 15 | 3 | 1 | Hz1 | Hz1 |  | uint16 | Hz | Hz_SF | RW | M | Point 1 must disconnect frequency.
Repeating Block |  | 16 | 4 | 1 | Fn1 | Fn1 |  | enum16 |  |  | RW | M | Point 1 special behavior.
Repeating Block |  | 17 | 5 | 2 | Tms2 | Tms2 |  | uint32 | Secs | Tms_SF | RW | O | Point 2 must disconnect duration.
Repeating Block |  | 19 | 7 | 1 | Hz2 | Hz2 |  | uint16 | Hz | Hz_SF | RW | O | Point 2 must disconnect frequency.
Repeating Block |  | 20 | 8 | 1 | Fn2 | Fn2 |  | enum16 |  |  | RW | O | Point 2 special behavior.
Repeating Block |  | 21 | 9 | 2 | Tms3 | Tms3 |  | uint32 | Secs | Tms_SF | RW | O | Point 3 must disconnect duration.
Repeating Block |  | 23 | 11 | 1 | Hz3 | Hz3 |  | uint16 | Hz | Hz_SF | RW | O | Point 3 must disconnect frequency.
Repeating Block |  | 24 | 12 | 1 | Fn3 | Fn3 |  | enum16 |  |  | RW | O | Point 3 special behavior.
Repeating Block |  | 25 | 13 | 2 | Tms4 | Tms4 |  | uint32 | Secs | Tms_SF | RW | O | Point 4 must disconnect duration.
Repeating Block |  | 27 | 15 | 1 | Hz4 | Hz4 |  | uint16 | Hz | Hz_SF | RW | O | Point 4 must disconnect frequency.
Repeating Block |  | 28 | 16 | 1 | Fn4 | Fn4 |  | enum16 |  |  | RW | O | Point 4 special behavior.
Repeating Block |  | 29 | 17 | 2 | Tms5 | Tms5 |  | uint32 | Secs | Tms_SF | RW | O | Point 5 must disconnect duration.
Repeating Block |  | 31 | 19 | 1 | Hz5 | Hz5 |  | uint16 | Hz | Hz_SF | RW | O | Point 5 must disconnect frequency.
Repeating Block |  | 32 | 20 | 1 | Fn5 | Fn5 |  | enum16 |  |  | RW | O | Point 5 special behavior.
Repeating Block |  | 33 | 21 | 2 | Tms6 | Tms6 |  | uint32 | Secs | Tms_SF | RW | O | Point 6 must disconnect duration.
Repeating Block |  | 35 | 23 | 1 | Hz6 | Hz6 |  | uint16 | Hz | Hz_SF | RW | O | Point 6 must disconnect frequency.
Repeating Block |  | 36 | 24 | 1 | Fn6 | Fn6 |  | enum16 |  |  | RW | O | Point 6 special behavior.
Repeating Block |  | 37 | 25 | 2 | Tms7 | Tms7 |  | uint32 | Secs | Tms_SF | RW | O | Point 7 must disconnect duration.
Repeating Block |  | 39 | 27 | 1 | Hz7 | Hz7 |  | uint16 | Hz | Hz_SF | RW | O | Point 7 must disconnect frequency.
Repeating Block |  | 40 | 28 | 1 | Fn7 | Fn7 |  | enum16 |  |  | RW | O | Point 7 special behavior.
Repeating Block |  | 41 | 29 | 2 | Tms8 | Tms8 |  | uint32 | Secs | Tms_SF | RW | O | Point 8 must disconnect duration.
Repeating Block |  | 43 | 31 | 1 | Hz8 | Hz8 |  | uint16 | Hz | Hz_SF | RW | O | Point 8 must disconnect frequency.
Repeating Block |  | 44 | 32 | 1 | Fn8 | Fn8 |  | enum16 |  |  | RW | O | Point 8 special behavior.
Repeating Block |  | 45 | 33 | 2 | Tms9 | Tms9 |  | uint32 | Secs | Tms_SF | RW | O | Point 9 must disconnect duration.
Repeating Block |  | 47 | 35 | 1 | Hz9 | Hz9 |  | uint16 | Hz | Hz_SF | RW | O | Point 9 must disconnect frequency.
Repeating Block |  | 48 | 36 | 1 | Fn9 | Fn9 |  | enum16 |  |  | RW | O | Point 9 special behavior.
Repeating Block |  | 49 | 37 | 2 | Tms10 | Tms10 |  | uint32 | Secs | Tms_SF | RW | O | Point 10 must disconnect duration.
Repeating Block |  | 51 | 39 | 1 | Hz10 | Hz10 |  | uint16 | Hz | Hz_SF | RW | O | Point 10 must disconnect frequency.
Repeating Block |  | 52 | 40 | 1 | Fn10 | Fn10 |  | enum16 |  |  | RW | O | Point 10 special behavior.
Repeating Block |  | 53 | 41 | 2 | Tms11 | Tms11 |  | uint32 | Secs | Tms_SF | RW | O | Point 11 must disconnect duration.
Repeating Block |  | 55 | 43 | 1 | Hz11 | Hz11 |  | uint16 | Hz | Hz_SF | RW | O | Point 11 must disconnect frequency.
Repeating Block |  | 56 | 44 | 1 | Fn11 | Fn11 |  | enum16 |  |  | RW | O | Point 11 special behavior.
Repeating Block |  | 57 | 45 | 2 | Tms12 | Tms12 |  | uint32 | Secs | Tms_SF | RW | O | Point 12 must disconnect duration.
Repeating Block |  | 59 | 47 | 1 | Hz12 | Hz12 |  | uint16 | Hz | Hz_SF | RW | O | Point 12 must disconnect frequency.
Repeating Block |  | 60 | 48 | 1 | Fn12 | Fn12 |  | enum16 |  |  | RW | O | Point 12 special behavior.
Repeating Block |  | 61 | 49 | 2 | Tms13 | Tms13 |  | uint32 | Secs | Tms_SF | RW | O | Point 13 must disconnect duration.
Repeating Block |  | 63 | 51 | 1 | Hz13 | Hz13 |  | uint16 | Hz | Hz_SF | RW | O | Point 13 must disconnect frequency.
Repeating Block |  | 64 | 52 | 1 | Fn13 | Fn13 |  | enum16 |  |  | RW | O | Point 13 special behavior.
Repeating Block |  | 65 | 53 | 2 | Tms14 | Tms14 |  | uint32 | Secs | Tms_SF | RW | O | Point 14 must disconnect duration.
Repeating Block |  | 67 | 55 | 1 | Hz14 | Hz14 |  | uint16 | Hz | Hz_SF | RW | O | Point 14 must disconnect frequency.
Repeating Block |  | 68 | 56 | 1 | Fn14 | Fn14 |  | enum16 |  |  | RW | O | Point 14 special behavior.
Repeating Block |  | 69 | 57 | 2 | Tms15 | Tms15 |  | uint32 | Secs | Tms_SF | RW | O | Point 15 must disconnect duration.
Repeating Block |  | 71 | 59 | 1 | Hz15 | Hz15 |  | uint16 | Hz | Hz_SF | RW | O | Point 15 must disconnect frequency.
Repeating Block |  | 72 | 60 | 1 | Fn15 | Fn15 |  | enum16 |  |  | RW | O | Point 15 special behavior.
Repeating Block |  | 73 | 61 | 2 | Tms16 | Tms16 |  | uint32 | Secs | Tms_SF | RW | O | Point 16 must disconnect duration.
Repeating Block |  | 75 | 63 | 1 | Hz16 | Hz16 |  | uint16 | Hz | Hz_SF | RW | O | Point 16 must disconnect frequency.
Repeating Block |  | 76 | 64 | 1 | Fn16 | Fn16 |  | enum16 |  |  | RW | O | Point 16 special behavior.
Repeating Block |  | 77 | 65 | 2 | Tms17 | Tms17 |  | uint32 | Secs | Tms_SF | RW | O | Point 17 must disconnect duration.
Repeating Block |  | 79 | 67 | 1 | Hz17 | Hz17 |  | uint16 | Hz | Hz_SF | RW | O | Point 17 must disconnect frequency.
Repeating Block |  | 80 | 68 | 1 | Fn17 | Fn17 |  | enum16 |  |  | RW | O | Point 17 special behavior.
Repeating Block |  | 81 | 69 | 2 | Tms18 | Tms18 |  | uint32 | Secs | Tms_SF | RW | O | Point 18 must disconnect duration.
Repeating Block |  | 83 | 71 | 1 | Hz18 | Hz18 |  | uint16 | Hz | Hz_SF | RW | O | Point 18 must disconnect frequency.
Repeating Block |  | 84 | 72 | 1 | Fn18 | Fn18 |  | enum16 |  |  | RW | O | Point 18 special behavior.
Repeating Block |  | 85 | 73 | 2 | Tms19 | Tms19 |  | uint32 | Secs | Tms_SF | RW | O | Point 19 must disconnect duration.
Repeating Block |  | 87 | 75 | 1 | Hz19 | Hz19 |  | uint16 | Hz | Hz_SF | RW | O | Point 19 must disconnect frequency.
Repeating Block |  | 88 | 76 | 1 | Fn19 | Fn19 |  | enum16 |  |  | RW | O | Point 19 special behavior.
Repeating Block |  | 89 | 77 | 2 | Tms20 | Tms20 |  | uint32 | Secs | Tms_SF | RW | O | Point 20 must disconnect duration.
Repeating Block |  | 91 | 79 | 1 | Hz20 | Hz20 |  | uint16 | Hz | Hz_SF | RW | O | Point 20 must disconnect frequency.
Repeating Block |  | 92 | 80 | 1 | Fn20 | Fn20 |  | enum16 |  |  | RW | O | Point 20 special behavior.
Repeating Block |  | 93 | 81 | 8 | CrvNam | CrvNam |  | string |  |  | RW | O | Optional description for curve.
Repeating Block |  | 101 | 89 | 1 | ReadOnly | ReadOnly |  | enum16 |  |  | R | M | Enumerated value indicates if curve is read-only or can be modified.
bitfield16 | ModEna |  |  | Name: ENABLED; Value: 0
enum16 | Fn1 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn2 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn3 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn4 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn5 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn6 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn7 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn8 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn9 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn10 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn11 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn12 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn13 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn14 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn15 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn16 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn17 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn18 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn19 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | Fn20 |  |  | Name: CEASE_TO_ENERGIZE; Value: 1
enum16 | ReadOnly |  |  | Name: READWRITE; Value: 0
enum16 | ReadOnly |  |  | Name: READONLY; Value: 1