## Index
Model | Label | Description | Notes
802 | Battery Base Model
64200 | Pika Energy Device Directory | Pika Vendor model for LCM | Use this model to to read and change the system operating mode (sysmode), determine which devices are on the REbus system, read device status updates, enable/disable devices, and get each device's Modbus unit ID (aka slave ID).
64201 | Pika Energy Inverter Export model | Pika Vendor model for inverters with current transducers
64202 | Pika Energy Inverter Arbitrage Control | Power control model for Energy Island
64203 | Pika Energy Reconnect Control | Define grid parameters required for reconnection

## 802
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Battery Base Model | 802 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 62 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | AHRtg | Nameplate Charge Capacity |  | uint16 | Ah | AHRtg_SF | R | M | Nameplate charge capacity in amp-hours.
Fixed Block |  | 3 | 1 | 1 | WHRtg | Nameplate Energy Capacity |  | uint16 | Wh | WHRtg_SF | R | M | Nameplate energy capacity in DC watt-hours.
Fixed Block |  | 4 | 2 | 1 | WChaRteMax | Nameplate Max Charge Rate |  | uint16 | W | WChaDisChaMax_SF | RW | M | Maximum rate of energy transfer into the storage device in DC watts.
Fixed Block |  | 5 | 3 | 1 | WDisChaRteMax | Namplate Max Discharge Rate |  | uint16 | W | WChaDisChaMax_SF | RW | M | Maximum rate of energy transfer out of the storage device in DC watts.
Fixed Block |  | 6 | 4 | 1 | DisChaRte | Self Discharge Rate |  | uint16 | %WHRtg | DisChaRte_SF | R | O | Self discharge rate. Percentage of capacity (WHRtg) discharged per day.
Fixed Block |  | 7 | 5 | 1 | SoCMax | Nameplate Max SoC |  | uint16 | %WHRtg | SoC_SF | RW | O | Manufacturer maximum state of charge, expressed as a percentage.
Fixed Block |  | 8 | 6 | 1 | SoCMin | Nameplate Min SoC |  | uint16 | %WHRtg | SoC_SF | RW | O | Manufacturer minimum state of charge, expressed as a percentage.
Fixed Block |  | 9 | 7 | 1 | SocRsvMax | Max Reserve Percent |  | uint16 | %WHRtg | SoC_SF | RW | O | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage.
Fixed Block |  | 10 | 8 | 1 | SoCRsvMin | Min Reserve Percent |  | uint16 | %WHRtg | SoC_SF | RW | O | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage.
Fixed Block |  | 11 | 9 | 1 | SoC | State of Charge |  | uint16 | %WHRtg | SoC_SF | R | M | State of charge, expressed as a percentage. | Measurement.
Fixed Block |  | 12 | 10 | 1 | DoD | Depth of Discharge |  | uint16 | % | DoD_SF | R | O | Depth of discharge, expressed as a percentage. | Measurement.
Fixed Block |  | 13 | 11 | 1 | SoH | State of Health |  | uint16 | % | SoH_SF | R | O | Percentage of battery life remaining.
Fixed Block |  | 14 | 12 | 2 | NCyc | Cycle Count |  | uint32 |  |  | R | O | Number of cycles executed in the battery.
Fixed Block |  | 16 | 14 | 1 | ChaSt | Charge Status |  | enum16 |  |  | R | O | Charge status of storage device. Enumeration.
Fixed Block |  | 17 | 15 | 1 | LocRemCtl | Control Mode |  | enum16 |  |  | R | M | Battery control mode. Enumeration. | Maps to DRCC.LocRemCtl in IEC 61850.
Fixed Block |  | 18 | 16 | 1 | Hb | Battery Heartbeat |  | uint16 |  |  | R | O | Value is incremented every second with periodic resets to zero.
Fixed Block |  | 19 | 17 | 1 | CtrlHb | Controller Heartbeat |  | uint16 |  |  | RW | O | Value is incremented every second with periodic resets to zero.
Fixed Block |  | 20 | 18 | 1 | AlmRst | Alarm Reset |  | uint16 |  |  | RW | M | Used to reset any latched alarms. 1 = Reset. | Battery should reset to 0 when reset is complete.
Fixed Block |  | 21 | 19 | 1 | Typ | Battery Type |  | enum16 |  |  | R | M | Type of battery. Enumeration. | Maps to DBAT.BatTyp in 61850.
Fixed Block |  | 22 | 20 | 1 | State | State of the Battery Bank |  | enum16 |  |  | R | M | State of the battery bank. Enumeration. | Must be reconciled with State in IEC 61850.
Fixed Block |  | 23 | 21 | 1 | Pad1 | Pad |  | pad |  |  | R | M | Pad register.
Fixed Block |  | 24 | 22 | 2 | WarrDt | Warranty Date |  | uint32 |  |  | R | O | Date the device warranty expires. | Number of days since 1/1/2000.
Fixed Block |  | 26 | 24 | 2 | Evt1 | Battery Event 1 Bitfield |  | bitfield32 |  |  | R | M | Alarms and warnings. Bit flags.
Fixed Block |  | 28 | 26 | 2 | Evt2 | Battery Event 2 Bitfield |  | bitfield32 |  |  | R | M | Alarms and warnings. Bit flags. | Reserved for future use.
Fixed Block |  | 30 | 28 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | M | Vendor defined events.
Fixed Block |  | 32 | 30 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | M | Vendor defined events.
Fixed Block |  | 34 | 32 | 1 | V | External Battery Voltage |  | uint16 | V | V_SF | R | M | DC Bus Voltage. | Maps to ZBAT.V in IEC 61850.
Fixed Block |  | 35 | 33 | 1 | VMax | Max Battery Voltage |  | uint16 | V | V_SF | R | O | Instantaneous maximum battery voltage. | If not implemented, must implement AChaMax and ADisChaMax.
Fixed Block |  | 36 | 34 | 1 | VMin | Min Battery Voltage |  | uint16 | V | V_SF | R | O | Instantaneous minimum battery voltage. | If not implemented, must implement AChaMax and ADisChaMax.
Fixed Block |  | 37 | 35 | 1 | CellVMax | Max Cell Voltage |  | uint16 | V | CellV_SF | R | O | Maximum voltage for all cells in the bank. | Measurement.
Fixed Block |  | 38 | 36 | 1 | CellVMaxStr | Max Cell Voltage String |  | uint16 |  |  | R | O | String containing the cell with maximum voltage.
Fixed Block |  | 39 | 37 | 1 | CellVMaxMod | Max Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with maximum voltage.
Fixed Block |  | 40 | 38 | 1 | CellVMin | Min Cell Voltage |  | uint16 | V | CellV_SF | R | O | Minimum voltage for all cells in the bank. | Measurement.
Fixed Block |  | 41 | 39 | 1 | CellVMinStr | Min Cell Voltage String |  | uint16 |  |  | R | O | String containing the cell with minimum voltage.
Fixed Block |  | 42 | 40 | 1 | CellVMinMod | Min Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with minimum voltage.
Fixed Block |  | 43 | 41 | 1 | CellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | O | Average cell voltage for all cells in the bank. | Calculation based on measurements.
Fixed Block |  | 44 | 42 | 1 | A | Total DC Current |  | int16 | A | A_SF | R | M | Total DC current flowing to/from the battery bank. | Measurement.
Fixed Block |  | 45 | 43 | 1 | AChaMax | Max Charge Current |  | uint16 | A | AMax_SF | R | O | Instantaneous maximum DC charge current. | Calculation. If not implemented, must implement VMax and VMin.
Fixed Block |  | 46 | 44 | 1 | ADisChaMax | Max Discharge Current |  | uint16 | A | AMax_SF | R | O | Instantaneous maximum DC discharge current. | Calculation. If not implemented, must implement VMax and VMin.
Fixed Block |  | 47 | 45 | 1 | W | Total Power |  | int16 | W | W_SF | R | M | Total power flowing to/from the battery bank. | Measurement.
Fixed Block |  | 48 | 46 | 1 | ReqInvState | Inverter State Request |  | enum16 |  |  | R | O | Request from battery to start or stop the inverter. Enumeration. | Used in special states such as manual battery charging.
Fixed Block |  | 49 | 47 | 1 | ReqW | Battery Power Request |  | int16 | W | W_SF | R | O | AC Power requested by battery. | Used in special states such as string balancing.
Fixed Block |  | 50 | 48 | 1 | SetOp | Set Operation |  | enum16 |  |  | RW | M | Instruct the battery bank to perform an operation such as connecting. Enumeration.
Fixed Block |  | 51 | 49 | 1 | SetInvState | Set Inverter State |  | enum16 |  |  | RW | M | Set the current state of the inverter. | Information needed by battery for some operations.
Fixed Block |  | 52 | 50 | Size: 1; Name: AHRtg_SF; Type: sunssf; R/W: R | M | Scale factor for charge capacity.
Fixed Block |  | 53 | 51 | Size: 1; Name: WHRtg_SF; Type: sunssf; R/W: R | M | Scale factor for energy capacity.
Fixed Block |  | 54 | 52 | Size: 1; Name: WChaDisChaMax_SF; Type: sunssf; R/W: R | M | Scale factor for maximum charge and discharge rate.
Fixed Block |  | 55 | 53 | Size: 1; Name: DisChaRte_SF; Type: sunssf; R/W: R | O | Scale factor for self discharge rate.
Fixed Block |  | 56 | 54 | Size: 1; Name: SoC_SF; Type: sunssf; R/W: R | M | Scale factor for state of charge values.
Fixed Block |  | 57 | 55 | Size: 1; Name: DoD_SF; Type: sunssf; R/W: R | O | Scale factor for depth of discharge.
Fixed Block |  | 58 | 56 | Size: 1; Name: SoH_SF; Type: sunssf; R/W: R | O | Scale factor for state of health.
Fixed Block |  | 59 | 57 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M | Scale factor for DC bus voltage.
Fixed Block |  | 60 | 58 | Size: 1; Name: CellV_SF; Type: sunssf; R/W: R | M | Scale factor for cell voltage.
Fixed Block |  | 61 | 59 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Scale factor for DC current.
Fixed Block |  | 62 | 60 | Size: 1; Name: AMax_SF; Type: sunssf; R/W: R | M | Scale factor for instantationous DC charge/discharge current.
Fixed Block |  | 63 | 61 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | O | Scale factor for AC power request.
enum16 | ChaSt |  |  | Name: OFF; Value: 1
enum16 | ChaSt |  |  | Name: EMPTY; Value: 2
enum16 | ChaSt |  |  | Name: DISCHARGING; Value: 3
enum16 | ChaSt |  |  | Name: CHARGING; Value: 4
enum16 | ChaSt |  |  | Name: FULL; Value: 5
enum16 | ChaSt |  |  | Name: HOLDING; Value: 6
enum16 | ChaSt |  |  | Name: TESTING; Value: 7
enum16 | LocRemCtl |  |  | Name: REMOTE; Label: Remote Control; Value: 0 |  | Battery is controlled remotely (e.g. by the site controller). | Value of 0 matches LocRemCtl in IEC 61850.
enum16 | LocRemCtl |  |  | Name: LOCAL; Label: Local Control; Value: 1 |  | Battery is controlled by a local operator (e.g. through battery HMI). | Value of 1 matches LocRemCtl in IEC 61850.
enum16 | Typ |  |  | Name: NOT APPLICABLE_UNKNOWN; Label: Not Applicable or Unknown; Value: 0 |  | Battery type is not applicable or unknown.
enum16 | Typ |  |  | Name: LEAD_ACID; Label: Lead-Acid; Value: 1 |  | Lead-acid battery type.
enum16 | Typ |  |  | Name: NICKEL_METAL_HYDRATE; Label: Nickel-Metal Hydrate; Value: 2 |  | Nickel-metal hydrate battery type.
enum16 | Typ |  |  | Name: NICKEL_CADMIUM; Label: Nickel-Cadmium; Value: 3 |  | Nickel-cadmium battery type.
enum16 | Typ |  |  | Name: LITHIUM_ION; Label: Lithium-Ion; Value: 4 |  | Lithium-ion battery type.
enum16 | Typ |  |  | Name: CARBON_ZINC; Label: Carbon-Zinc; Value: 5 |  | Carbon-zinc battery type.
enum16 | Typ |  |  | Name: ZINC_CHLORIDE; Label: Zinc Chloride; Value: 6 |  | Zinc chloride battery type.
enum16 | Typ |  |  | Name: ALKALINE; Label: Alkaline; Value: 7 |  | Alkaline battery type.
enum16 | Typ |  |  | Name: RECHARGEABLE_ALKALINE; Label: Rechargeable Alkaline; Value: 8 |  | Rechargeable alkaline battery type.
enum16 | Typ |  |  | Name: SODIUM_SULFUR; Label: Sodium-Sulfur; Value: 9 |  | Sodium-sulfur battery type.
enum16 | Typ |  |  | Name: FLOW; Label: Flow; Value: 10 |  | Flow battery type.
enum16 | Typ |  |  | Name: OTHER; Label: Other; Value: 99 |  | Other battery type.
enum16 | State |  |  | Name: DISCONNECTED; Label: Disconnected; Value: 1 |  | Battery bank is disconnected. All contactors are open.
enum16 | State |  |  | Name: INITIALIZING; Label: Initializing; Value: 2 |  | Battery bank is initializing but not ready for operating. String balancing may occur.
enum16 | State |  |  | Name: CONNECTED; Label: Connected; Value: 3 |  | Battery bank is ready for operation. All enabled contactors are closed.
enum16 | State |  |  | Name: STANDBY; Label: Standby; Value: 4 |  | Battery bank is connected and in standby/power saving mode.
enum16 | State |  |  | Name: SOC PROTECTION; Label: SoC Protection; Value: 5 |  | Battery bank is connected but SoC is too low. Battery should be considered "offline".
enum16 | State |  |  | Name: FAULT; Label: Fault; Value: 99 |  | The battery has experienced a critical failure and may not be operated.
bitfield32 | Evt1 |  |  | Name: COMMUNICATION_ERROR; Label: Communication Error; Value: 0 |  | Unable to communcate with BMS or BMS is unable to communicate with battery strings.
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_ALARM; Label: Over Temperature Alarm; Value: 1 |  | Battery has exceeded maximum operating temperature
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_WARNING; Label: Over Temperature Warning; Value: 2 |  | Battery is approaching maximum operating temperature.
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_ALARM; Label: Under Temperature Alarm; Value: 3 |  | Battery has exceeded minimum operating temperature
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_WARNING; Label: Under Temperature Warning; Value: 4 |  | Battery is approaching minimum operating temperature.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_ALARM; Label: Over Charge Current Alarm; Value: 5 |  | Battery maximum charge current has been exceeded. | See AChaMax.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_WARNING; Label: Over Charge Current Warning; Value: 6 |  | Approaching battery maximum charge current. | See AChaMax.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_ALARM; Label: Over Discharge Current Alarm; Value: 7 |  | Battery maximum discharge current has been exceeded. | See ADisChaMax.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_WARNING; Label: Over Discharge Current Warning; Value: 8 |  | Approaching battery maximum discharge current. | See ADisChaMax.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_ALARM; Label: Over Voltage Alarm; Value: 9 |  | Battery voltage has exceeded maximum limit.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_WARNING; Label: Over Voltage Warning; Value: 10 |  | Battery voltage is approaching maximum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_ALARM; Label: Under Voltage Alarm; Value: 11 |  | Battery voltage has exceeded minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_WARNING; Label: Under Voltage Warning; Value: 12 |  | Battery voltage is approaching minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_ALARM; Label: Under State of Charge Min Alarm; Value: 13 |  | Battery state of charge has reached or exceeded SoCMin
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_WARNING; Label: Under State of Charge Min Warning; Value: 14 |  | Battery state of charge is approaching SoCMin
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_ALARM; Label: Over State of Charge Max Alarm; Value: 15 |  | Battery state of charge has reached or exceeded SoCMax
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_WARNING; Label: Over State of Charge Max Warning; Value: 16 |  | Battery state of charge is approaching SoCMax
bitfield32 | Evt1 |  |  | Name: VOLTAGE_IMBALANCE_WARNING; Label: Voltage Imbalance Warning; Value: 17 |  | A voltage imbalance exists between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: TEMPERATURE_IMBALANCE_ALARM; Label: Temperature Imbalance Alarm; Value: 18 |  | A temperature imbalance exists between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: TEMPERATURE_IMBALANCE_WARNING; Label: Temperature Imbalance Warning; Value: 19 |  | A temperature imbalance is developing between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: CONTACTOR_ERROR; Label: Contactor Error; Value: 20 |  | A contactor failed to open or close as requested.
bitfield32 | Evt1 |  |  | Name: FAN_ERROR; Label: Fan Error; Value: 21 |  | One or more battery fans has failed.
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground Fault Error; Value: 22 |  | Ground fault detected.
bitfield32 | Evt1 |  |  | Name: OPEN_DOOR_ERROR; Label: Open Door Error; Value: 23 |  | One or more doors are open.
bitfield32 | Evt1 |  |  | Name: CURRENT_IMBALANCE_WARNING; Label: Current Imbalance Warning; Value: 24 |  | A current imbalance exists between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: OTHER_ALARM; Label: Other Battery Alarm; Value: 25 |  | A vendor specific alarm has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | Evt1 |  |  | Name: OTHER_WARNING; Label: Other Battery Warning; Value: 26 |  | A vendor specific warning has occurred. | See EvtVnd1 and EvtVnd2 for more information.
enum16 | ReqInvState |  |  | Name: NO REQUEST; Label: No Request; Value: 0 |  | Battery has no requests of the inverter.
enum16 | ReqInvState |  |  | Name: START; Label: Start Inverter; Value: 1 |  | Battery requests that the inverter be started. | Battery is notified of inverter state change through SetInvState.
enum16 | ReqInvState |  |  | Name: STOP; Label: Stop Inverter; Value: 2 |  | Battery requests that the inverter be stopped. | Battery is notified of inverter state change through SetInvState.
enum16 | SetOp |  |  | Name: CONNECT; Label: Connect the Battery Bank; Value: 1 |  | Initialize the battery bank and close contactors for all enabled strings.
enum16 | SetOp |  |  | Name: DISCONNECT; Label: Disconnect the Battery Bank; Value: 2 |  | Open contactors for all strings.
enum16 | SetInvState |  |  | Name: INVERTER_STOPPED; Label: Inverter is Stopped; Value: 1
enum16 | SetInvState |  |  | Name: INVERTER_STANDBY; Label: Inverter is in Standby; Value: 2
enum16 | SetInvState |  |  | Name: INVERTER_STARTED; Label: Inverter is Started; Value: 3

## 64200
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Pika Energy Device Directory | 64200 | uint16 |  |  | R | M | Pika Vendor model for LCM | Use this model to to read and change the system operating mode (sysmode), determine which devices are on the REbus system, read device status updates, enable/disable devices, and get each device's Modbus unit ID (aka slave ID).
Header |  | 1 |  | 1 | L |  | 8 + (RB Count * 32) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | UpdtN | Update number |  | uint16 |  |  | R | M | Update Number. Incrementing number each time the mappping is changed. If the number is not changed from the last reading then none of the Modbus device addresses have changed.
Fixed Block |  | 3 | 1 | 1 | Ct | Device count |  | uint16 |  |  | R | M | The number of connected devices (and repetitions of repeating block)
Fixed Block |  | 4 | 2 | 1 | SysMd | System Operating Mode |  | enum16 |  |  | RW | M | REbus System mode (sysmode), also known as the operational mode | See X7601 Operation Manual for details on the REbus operational modes
Fixed Block |  | 5 | 3 | 1 | VT_sf | VT_sf |  | sunssf |  |  | R | M | Scale factor for V and T of repeating block
Fixed Block |  | 6 | 4 | 1 | I_sf | I_sf |  | sunssf |  |  | R | M | Scale factor for I of repeating block
Fixed Block |  | 7 | 5 | 2 | Time | Current system time |  | uint32 | s |  | R | M | Unix epoch time
Fixed Block |  | 9 | 7 | 1 | Clr | Clear device list |  | uint16 |  |  | RW | M |  | online devices will reappear momentarily after clearing
Repeating Block |  | 10 | 0 | 1 | Man | Manufacturer |  | uint16 |  |  | R | M | RCP number (manufacturer)
Repeating Block |  | 11 | 1 | 1 | Dev | Device Type |  | uint16 |  |  | R | M | RCP number (device type)
Repeating Block |  | 12 | 2 | 1 | ID | Device ID |  | uint16 |  |  | R | M | RCP number (device ID)
Repeating Block |  | 13 | 3 | 1 | Ena | Enable |  | enum16 |  |  | RW | M | enable/disable device
Repeating Block |  | 14 | 4 | 1 | UnitID | ModBus ID |  | uint16 |  |  | R | M | Modbus unit identifier
Repeating Block |  | 15 | 5 | 2 | UpdtTm | Update Time |  | uint32 | s |  | R | M | Time of last update (Unix epoch time)
Repeating Block |  | 17 | 7 | 1 | St | State |  | uint16 |  |  | R | M |  | State is a status field used by Pika Energy for operations and maintenance purposes
Repeating Block |  | 18 | 8 | 1 | P | REbus Power |  | int16 | W |  | R | M | REbus power (positive means the device is sourcing power onto REbus, negative means the device is sinking power from REbus)
Repeating Block |  | 19 | 9 | 2 | E | Accumulated Energy |  | uint32 | Wh |  | R | M | Total accumulated energy (exact definition differs by device)
Repeating Block |  | 21 | 11 | 1 | Rb | REbus Bits |  | uint16 |  |  | R | M |  | REbusBits is a status field used by Pika Energy for operations and maintenance purposes
Repeating Block |  | 22 | 12 | 1 | V | REbus Voltage |  | uint16 | V | VT_sf | R | M | REbus voltage in V*10
Repeating Block |  | 23 | 13 | 1 | I | REbus Current |  | uint16 | A | I_sf | R | M | REbus current in A*10
Repeating Block |  | 24 | 14 | 1 | T | Device Temperature |  | uint16 | °C | VT_sf | R | M | Device temperature in C*10
Repeating Block |  | 25 | 15 | 1 | O0 | Otherdata 0 |  | uint16 |  |  | R | M | Otherdata 0
Repeating Block |  | 26 | 16 | 1 | O1 | Otherdata 1 |  | uint16 |  |  | R | M | Otherdata 1
Repeating Block |  | 27 | 17 | 1 | O2 | Otherdata 2 |  | uint16 |  |  | R | M | Otherdata 2
Repeating Block |  | 28 | 18 | 1 | O3 | Otherdata 3 |  | uint16 |  |  | R | M | Otherdata 3
Repeating Block |  | 29 | 19 | 1 | O4 | Otherdata 4 |  | uint16 |  |  | R | M | Otherdata 4
Repeating Block |  | 30 | 20 | 1 | O5 | Otherdata 5 |  | uint16 |  |  | R | M | Otherdata 5
Repeating Block |  | 31 | 21 | 1 | O6 | Otherdata 6 |  | uint16 |  |  | R | M | Otherdata 6
Repeating Block |  | 32 | 22 | 1 | O7 | Otherdata 7 |  | uint16 |  |  | R | M | Otherdata 7
Repeating Block |  | 33 | 23 | 1 | O8 | Otherdata 8 |  | uint16 |  |  | R | M | Otherdata 8
Repeating Block |  | 34 | 24 | 1 | O9 | Otherdata 9 |  | uint16 |  |  | R | M | Otherdata 9
Repeating Block |  | 35 | 25 | 1 | OA | Otherdata A |  | uint16 |  |  | R | M | Otherdata A
Repeating Block |  | 36 | 26 | 1 | OB | Otherdata B |  | uint16 |  |  | R | M | Otherdata B
Repeating Block |  | 37 | 27 | 1 | OC | Otherdata C |  | uint16 |  |  | R | M | Otherdata C
Repeating Block |  | 38 | 28 | 1 | OD | Otherdata D |  | uint16 |  |  | R | M | Otherdata D
Repeating Block |  | 39 | 29 | 1 | OE | Otherdata E |  | uint16 |  |  | R | M | Otherdata E
Repeating Block |  | 40 | 30 | 1 | OF | Otherdata F |  | uint16 |  |  | R | M | Otherdata F
Repeating Block |  | 41 | 31 | 1 | OG | Otherdata G |  | uint16 |  |  | R | M | Otherdata G
enum16 | SysMd |  |  | Name: SAFETY_SHUTDOWN; Value: 0
enum16 | SysMd |  |  | Name: GRID_CONNECT; Value: 1
enum16 | SysMd |  |  | Name: SELF_SUPPLY; Value: 2
enum16 | SysMd |  |  | Name: CLEAN_BACKUP; Value: 3
enum16 | SysMd |  |  | Name: PRIORITY_BACKUP; Value: 4
enum16 | SysMd |  |  | Name: ARBITRAGE; Value: 5

## 64201
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Pika Energy Inverter Export model | 64201 | uint16 |  |  | R | M | Pika Vendor model for inverters with current transducers
Header |  | 1 |  | 1 | L |  | 6 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Px1 | Power export line 1 |  | int16 | W |  | R | M | RMS power to/from grid on line 1 | if no CTs connected, this value will be 0x8000
Fixed Block |  | 3 | 1 | 1 | Px2 | Power export line 2 |  | int16 | W |  | R | M | RMS power to/from grid on line 2 | if no CTs connected, this value will be 0x8000
Fixed Block |  | 4 | 2 | 2 | Whx | Energy exported |  | acc32 | Wh |  | R | M | Energy exported to grid
Fixed Block |  | 6 | 4 | 2 | Whin | Energy imported |  | acc32 | Wh |  | R | M | Total imported energy to REbus | does not include local loads

## 64202
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Pika Energy Inverter Arbitrage Control | 64202 | uint16 |  |  | R | M | Power control model for Energy Island
Header |  | 1 |  | 1 | L |  | 12 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | SysMd | System Operating Mode |  | enum16 |  |  | R | M | System operating mode | must be in Sysmode 5, ARBITRAGE, for the controls in this model to take effect. It is read-only in this model. This parameter can be changed from model 64200 on the device at Modbus slave ID 1
Fixed Block |  | 3 | 1 | 1 | PMax | Max real power |  | uint16 |  | PQMax_SF | RW | M | Maximum real power magnitude | applies to import and export power levels
Fixed Block |  | 4 | 2 | 1 | QMax | Max reactive power |  | uint16 |  | PQMax_SF | RW | M | Maximum reactive power magnitude | applies to import and export power levels
Fixed Block |  | 5 | 3 | 1 | PMaxLimPct | Real power target |  | int16 |  | PQLimPct_SF | RW | M | target real power - -100.0% to +100.0% of PMax | take note of scale factor: -1000 to 1000 corresponds to -100.0% to 100.0%
Fixed Block |  | 6 | 4 | 1 | QMaxLimPct | Reactive power target |  | int16 |  | PQLimPct_SF | RW | M | target reactive power - -100.0% to +100.0% of QMax | take note of scale factor: -1000 to 1000 corresponds to -100.0% to 100.0%
Fixed Block |  | 7 | 5 | 1 | PQGra | Ramp rate |  | uint16 |  | PQGra_SF | RW | M | ramp rate for slewing power to target | applies to both active and reactive slewing
Fixed Block |  | 8 | 6 | 1 | PQMax_SF | PQMax_SF |  | sunssf |  |  | R | M | scale factor for max power | applies to both active and reactive power levels
Fixed Block |  | 9 | 7 | 1 | PQLimPct_SF | PQLimPct_SF |  | sunssf |  |  | R | M | scale factor for target power percentages | applies to both active and reactive power levels
Fixed Block |  | 10 | 8 | 1 | PQGra_SF | PQGra_SF |  | sunssf |  |  | R | M | scale factor for ramp rate
Fixed Block |  | 11 | 9 | 1 | CtlPr | Control priority |  | enum16 |  |  | RW | M | set control priority to real or reactive target
Fixed Block |  | 12 | 10 | 1 | PQSet_Ena | Enable arbitrage control |  | enum16 |  |  | RW | M | activate PQ control settings | must set this flag to ENABLE or UPDATE for new settings to take effect
Fixed Block |  | 13 | 11 | 1 | Conn | Connect |  | enum16 |  |  | RW | M | enable/disable inverter
enum16 | SysMd |  |  | Name: SAFETY_SHUTDOWN; Value: 0
enum16 | SysMd |  |  | Name: GRID_CONNECT; Value: 1
enum16 | SysMd |  |  | Name: SELF_SUPPLY; Value: 2
enum16 | SysMd |  |  | Name: CLEAN_BACKUP; Value: 3
enum16 | SysMd |  |  | Name: PRIORITY_BACKUP; Value: 4
enum16 | SysMd |  |  | Name: ARBITRAGE; Value: 5
enum16 | CtlPr |  |  | Name: REAL; Value: 0
enum16 | CtlPr |  |  | Name: REACTIVE; Value: 1
enum16 | PQSet_Ena |  |  | Name: DISABLE; Value: 0
enum16 | PQSet_Ena |  |  | Name: ENABLE; Value: 1
enum16 | PQSet_Ena |  |  | Name: UPDATE; Value: 2
enum16 | Conn |  |  | Name: DISCONNECT; Value: 0
enum16 | Conn |  |  | Name: CONNECT; Value: 1

## 64203
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Pika Energy Reconnect Control | 64203 | uint16 |  |  | R | M | Define grid parameters required for reconnection
Header |  | 1 |  | 1 | L |  | 10 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ModEna | ModEna |  | enum16 |  |  | RW | M | Enable this model's voltage and frequency window.
Fixed Block |  | 3 | 1 | 1 | ReConn_Tms | ReConn_Tms |  | uint16 | Secs | Tms_SF | RW | M | Time to reconnect after fault, and within frequency and voltage window.
Fixed Block |  | 4 | 2 | 1 | ReConnMinV | ReConnMinV |  | uint16 | %Vref | V_SF | RW | M | Reconnect only above this voltage
Fixed Block |  | 5 | 3 | 1 | ReConnMaxV | ReConnMaxV |  | uint16 | %Vref | V_SF | RW | M | Reconnect only below this voltage
Fixed Block |  | 6 | 4 | 1 | ReConnMinHz | ReConnMinHz |  | uint16 | Hz | Hz_SF | RW | M | Reconnect only above this frequency
Fixed Block |  | 7 | 5 | 1 | ReConnMaxHz | ReConnMaxHz |  | uint16 | Hz | Hz_SF | RW | M | Reconnect only below this frequency
Fixed Block |  | 8 | 6 | 1 | Tms_SF | Tms_SF |  | sunssf |  |  | R | M | Scale factor for reconnect time.
Fixed Block |  | 9 | 7 | 1 | V_SF | V_SF |  | sunssf |  |  | R | M | Scale factor for voltage percent of Vref.
Fixed Block |  | 10 | 8 | 1 | Hz_SF | Hz_SF |  | sunssf |  |  | R | M | Scale factor for frequency.
Fixed Block |  | 11 | 9 | Size: 1; Name: Pad; Type: pad; R/W: R | M
enum16 | ModEna |  |  | Name: DISABLE; Value: 0
enum16 | ModEna |  |  | Name: ENABLE; Value: 1